## Directions
START-UP: Settings: In Excel, Macro security: Tools - Macro - Security – Low In AutoCad, Set OLE link to “spreadsheet”, Tools - Options - Plot and Publish - OLE Plot Quality - Monochrome (e.g. spreadsheet) Hint: In “Notes” hold down ALT key and hit ENTER to move to next line.
FAULT: Get’s most of the information from the MDP tab. Can overwrite ANY value Example: If you get actual available fault on secondary of service transformer from utility, ENTER IT! Other info must be inserted are in blue. Shows formulas so you can double check with calculator. Impedance of wire (ft/ohms) automatically comes in. You can double check with table in Bussmann SPD. (4) boxes represent Utility Transformer Length of Feeder Interior transformer (typically 480:208) Motor load contribution May have to edit or move boxes around for your job. Feel free to edit large note cells.
MECH: Purpose is to easily compare with mech sheets. Automatically adds load (KVA) Automatically sizes feeders Needs work, voltage drop Input MCA/MOCP from mech Add notes Use loads automatically in MDP or panels
MDP & HA: MDP is EXACTLY like panels (HA) except: Special formatting showing all 3-poles Brings in Fault Calc automatically from FAULT Brings in load & OCPD from MECH Has feeders to panels & via transformer to pane Automatic buttons: (24P, 30P, 42P, etc.) to change # of poles on panel. What they do is HIDE rows. Play with buttons and check row numbers. Example: For 24P, rows numbered 14, 15, 16, 68, 69, 70 DON’T HIDE LOAD VALUES: Hidden rows still exist and will ADD to loads. Check by clicking 126P and make sure no loads are hidden. Fill out: Top: V, A, Lugs, Mount, Location, Int Cap
Middle: Load in KVA under correct heading (Ltg=continuous, Rec, HVAC, Misc=non-continuous, NP=Non-peak) Description: Use “REC” & “LTG” for receptacle and lighting. Keep it concise. Amp & Pole: Use “merge cells” when multi-pole, split loads per phase (non-merged) Notes: Add unique info per job Needs work, we need to standardize lock-on/off breakers, DELETE HACR BREAKER NOTES ON ALL JOBS, GFI breakers, etc. For reused panels, use Arial Black font as new, normal font as existing. Control: Have special buttons to turn on or off. Originally used to insert contactor numbers, but on some jobs we change this to “Notes” and put info in the notes. NEEDS WORK – CONSISTENCY
Bottom: Simply adds up loads. Typically no work. Improvements needed: Add demand load for show windows per NEC Add demand load for track ltg per NEC Very Bottom: Do not plot! This is for feeding panel to panel to simplify the process.
CONTACTORS & TRANSFORMERS These are “dumb” tables to be filled out if needed on a job. “Contactors” needs work: We can add automatic listing of circuit numbers with panels.
LOOKUP This is where automatic information comes from. Basically saves time by NOT having to open Bussmann SPD book or NEC for ampacity of conductors, grounding, conduit size. Needs Work: Need feedback from designers. WHAT TABLES DO YOU REFERENCE? Possibly add all possible feeder sizes with ground & conduit sizes. For jobs requiring feeder reference in panel schedule Possibly add lengths for V-drop calculations so automatically upsizes when design length is inserted.

## FEEDERS
Designer note: To get "LOAD, use "=" and go to "DEMAND AMPS" of associated panel. | [9 empty] | TOOL TO BE USED BY DESIGNERS, NOT INTENDED FOR DRAWINGS!
VOLTAGE DROP CALCULATIONS | [9 empty] | FEEDER INFORMATION |  | REMARKS |  | AL | =MATERIAL LOOKUP |  |  | AL TABLE= | A81:J114 | POSSIBLE VOLTAGES
PANEL | FEEDER |  | OHMS/K-FT NEC T9 | LENGTH | Z | LOAD | V-DROP | V | %V-DROP | OCPD FEEDING PANEL: | 400 | BY DESIGNER |  | CU |  |  |  | CU TABLE= | A115:J146 | 120/208
| AWG | SETS | [7 empty] | MATERIAL: | CU | BY DESIGNER | [7 empty] | 347/600
FC | 350 | 4 | 0.06 | 200 | 0.003 | 100 | 0.3 | 208 | 0.1442% | # PARALLEL SETS (Q) | 2 | TABLE 310.16 | TRANSFORMERS | [6 empty] | 120/240
? | 300 | 3 | 0.065 | 10 | 0.00021667 | 100 | 0.021667 | 277 | 0.007822% | FEEDER (AMPS): | 3/0 | TABLE 310.16 | XFRM | 600V FEED | MAX OCPD | FEEDER SIZE | 208V FEED | MAX OCPD | FEEDER SIZE
? | 300 | 3 | 0.065 | 10 | 0.00021667 | 100 | 0.021667 | 277 | 0.007822% | GROUND | 3 | EQ GND PER TABLE 250.122 | 15 | 18.0422 | 25 | (3)#10CU, #10CU G, 0.75''C | 52.0448 | 60 | (4)#4CU, #8CU G, 1.25''C
? | 2/0 | 1 | 0.11 | 10 | 0.0011 | 100 | 0.11 | 277 | 0.03971% | CONDUIT | 2.5 | INCH PER TABLE C9 PVC (WORST CASE) | 30 | 36.0844 | 50 | (3)#6CU, #10CU G, 1''C | 104.0896 | 110 | (4)#2CU, #8CU G, 1.5''C
? | 3 | 1 | 0.24 | 10 | 0.0024 | 100 | 0.24 | 277 | 0.08664% | FEEDER: | 2 SETS OF (4)#3/0CU, #3CU G, 2.5''C |  | 45 | 54.1266 | 70 | (3)#4CU, #8CU G, 1.25''C | 156.1344 | 175 | (4)#2/0CU, #6CU G, 2''C
? | 3/0 | 1 | 0.094 | 10 | 0.00094 | 100 | 0.094 | 277 | 0.03394% |  |  |  | 75 | 90.211 | 125 | (3)#1CU, #6CU G, 2''C | 260.224 | 300 | (4)#350CU, #1CU G, 3''C
? | 3 | 1 | 0.24 | 10 | 0.0024 | 100 | 0.24 | 277 | 0.08664% | VOLTAGE DROP INFORMATION |  | REMARKS | 112.5 | 135.3165 | 175 | (3)#2/0CU, #6CU G, 2''C | 390.336 | 400 | 2 SETS OF (4)#3/0CU, #6CU G, 2.5''C
NOTES: VOLTAGE DROP CALCULATIONS ARE BASED ON TABLE 9 OF THE NEC FOR EFFECTIVE Z AT 0.85 PF, UNCOATED COPPER WIRES IN STEEL CONDUIT (WORST CASE). LOAD IS THE DEMAND LOAD OF THE PANEL OR TRANSFORMER. EQUATION: Z = (OHMS/K-FT) * (K-FT/1000') * (LENGTH) / (SETS) V-DROP = Z * LOAD | [9 empty] | VOLTS | 347/600 | BY DESIGNER | 150 | 180.422 | 250 | (3)#250CU, #4CU G, 3''C | 520.448 | 600 | 2 SETS OF (4)#350CU, #1CU G, 3''C
[10 empty] | LOAD | 158 | BY DESIGNER | 225 | 270.6329 | 350 | (3)#500CU, #1CU G, 3.5''C | 780.6719 | 800 | 3 SETS OF (4)#300CU, #4CU G, 3''C
[10 empty] | V-DROP ALLOWED: | 3% | MAX PER ENERGY CODE, DESIGNER MAY EDIT | 300 | 360.8439 | 500 | 2 SETS OF (3)#250CU, #4CU G, 3''C | 1040.8959 | 1200 | 4 SETS OF (4)#350CU, #1CU G, 3''C
[11 empty] | 10.41 | PERCENTAGE OF VLN | 500 | 601.4065 | 800 | 3 SETS OF (3)#300CU, #4CU G, 3''C | 1734.8265 | 2000 | 6 SETS OF (4)#400CU, #1CU G, 3.5''C
[10 empty] | R ALLOWED TOTAL: | 0.065886 | =V-DROP/A | 750 | 902.1098 | 1200 | 4 SETS OF (3)#350CU, #1CU G, 3''C | 2602.2398 | 3000 | 8 SETS OF (4)#500CU, #1CU G, 3.5''C
[10 empty] | R ALLOWED PER SET: | 0.13177 | =R (total)*Q (parallel feeds; Rt=1/(1/R1+1/R2+...) | 1000 | 1202.8131 | 1600 | 5 SETS OF (3)#400CU, #1CU G, 3.5''C | 3469.6531 | 4000 | 11 SETS OF (4)#500CU, #1CU G, 3.5''C
[10 empty] | Z/1000' PER FEEDER: | 0.094 | FINDS Z/1000' FEEDER PER, IN OHMS/1000' | SEE NEC TABLE 450.3(B) FOR OVERCURRENT PROTECTION
[10 empty] | MAX LENGTH: | 1401.8314 | MAX L=R-ALL / (Z/1000') * 1000 | SEE NEC TABLE 250.66 FOR GROUNDING ELECTRODE CONDUCTOR
[6 empty] | PS 14K_CS_2025_Plumbing Schedule.xlsx |  |  |  | ACTUAL LENGTH | 152 | BY DESIGNER | FORMULA: KVA*1000/(VLL*SQRT(3))*1.25
[10 empty] | ACTUAL V-DROP % | 0.3253% | =[A*Z/1000')*Act L)/Q] / [VLN]
1401.8314
[10 empty] | ACTUAL LENGTH: | 386 | BY DESIGNER, USE IF MORE THAT MAX LENGTH
[10 empty] | # PARALLEL SETS (Q) | 1 | Q=(A/VDROP) * (Z#500 * L/1000)
[10 empty] | ACTUAL Z/1000' | 0.17069 | Z/1000' = V-DROP/(A/Q)/L*1000'
[10 empty] | FEEDER (Z/1000'): | 1 | CHECKS TABLE 9 & FINDS CONDUCTOR PER Z/1000'
[10 empty] | Z/1000' NEW FEEDER: | 0.16 | CHECKS TABLE 9 & FINDS Z/1000' PER CONDUCTOR
[10 empty] | ACTUAL V-DROP: | 9.7581 | V-DROP=(A/Q)*(Z/1000')*L/1000
[10 empty] | ACTUAL V-DROP %: | 2.812% | V-DROP % = V-DROP/VLN*100%
[10 empty] | GROUND | 6 | EQ GND PER TABLE 250.122
[10 empty] | CONDUIT | 2 | INCH PER TABLE C9 PVC (WORST CASE)
[10 empty] | FEEDER: | USE FEEDER ABOVE
STANDARD OCPD NEC 240.6
6000
5000
4000
3000
2500
2000
1600
1200
1000
800
700
600
500
450
400
350
300
250
225
200
175
150
125
110
100
90
80
70
60
50
45
35
30
25
20
15

## FAULT
|  |  |  | WIRE SIZE | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1 | 1/0 | 2/0 | 3/0 | 4/0 | 250 | 300 | 350 | 400 | 500 | 750
|  |  |  | MATERIAL | AL | CU
UTILITY TRANSFORMER FAULT CALCULATION |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx
SERVICE ENTRANCE |  | CALCULATION
VOLTAGE (L-L): | 600 | I-FLA=[RATED KVA * 1000]/ [V-LL*SQRT(PHASE)]
PHASE (PH): | 3
AMPS: | 400 | I-FLA= | 481.1252
FULL LOAD KVA: | 415.6922
TRANSFORMER: | 500 | M=100/%Z= | 76.9231
IMPEDANCE (%Z): | 1.3 | I-SC=I-FLA*M= | 37.0096
CALCULATION IS BASED ON ESTIMATED TRANSFORMER SIZE WITH %Z FROM BUSSMANN SPD. CONTRACTOR SHALL CONTACT UTILITY AND VERIFY I-SC AVAILABLE AT SECONDARY OF TRANSFORMER. CONTACT ENGINEER FOR RE-CALCULATION IF LARGER THAN CALCULATED.
MOTOR LOAD FAULT CALCULATION |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx
STARTING I-SC: | 37.0096 | CALCULATION
MOTOR LOAD (KVA): | 140.8869 | I-SC(ML)=I-ML*6= | 813.4109
MOTOR LOAD (A): | 135.5685 | I-SC=I-SC+I-SC(ML)= | 37.823
FEEDER FAULT CALCULATION |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx
STARTING I-SC: | 37.823 | IMPEDANCE BASED ON 3 SINGLE CONDUCTORS IN NON-MAGNETIC CONDUIT
VOLTAGE (L-L): | 600
PHASE (PH): | 3
FEEDER SIZE: | 250 | CALCULATION
FEEDER MATERIAL: | CU | *f=[SQRT(PHASE)*L*IS-C]/ [Q*C*V-LL]
PARALLEL SETS (Q): | 2
FEEDER LENGTH (L): | 100 | f= | 0.2936
FEET PER OHMS (C): | 18594 | M=1/(1+f)= | 0.77303
|  | I-SC=I-SC*M= | 29.2385
*f FOR SINGLE PHASE SYSTEMS, FEEDER LENGTH IS DOUBLED AND VOLTAGE IS LINE-NEUTRAL (OR V*LL/2)
STEP-DOWN TRANSFORMER FAULT CALCULATION |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx
STARTING I-SC: | 29.2385 | CALCULATION
VOLTAGE (PRI): | 600 | f=[I-SC(PRI)*V-PRI*SQRT(PHASE)*Z]/
VOLTAGE (SEC): | 208 | [KVA * 1000]
PHASE (PH): | 3 | f= | 6.8874
KVA TRANSFORMER | 150 | M=1/(1+f)= | 0.12678
%Z TRANSFORMER | 3.4% | I-SC=V-PRI/V-SEC*I-SC*M=
|  | I-SC= | 10.6932
3.4%Z MAXIMUM, CONTACT ENGINEER FOR RECALCULATION IF LESS.

## EQUIP
EQUIPMENT SCHEDULE
PLAN MARK | EQUIPMENT SERVED | LOAD | VOLT/ PHASE | FED BY | DISC BY | MCA | MOCPD | FEEDER | REMARKS |  |  | POLES
RTU-1 6 TONS) | ROOF TOP UNIT | 12.4708 | 600/3 | MDP | MC | 12 | 15 | (3)#12,#12G 1/2"C | CIRCUIT VIA "BOTTOM POWER ENTRY" KIT. COORDINATE WORK WITH RTU INSTALLER (TYPICAL) | POSSIBLE VOLTAGES |  | 3
RTU-2 (4 TONS) | ROOF TOP UNIT | 10.3923 | 600/3 | MDP | MC | 10 | 15 | (3)#12,#12G 1/2"C | (TYPICAL) | label | divider | 3
RTU-3 (5 TONS) | ROOF TOP UNIT | 12.4708 | 600/3 | MDP | MC | 12 | 15 | (3)#12,#12G 1/2"C | (TYPICAL) | 120/1 | 120 | 3
RTU-4 (7.5 TONS) | ROOF TOP UNIT | 17.6669 | 600/3 | MDP | MC | 17 | 20A | #N/A | (TYPICAL) | 208/1 | 208 | 3
RTU-5 (4 TONS) | ROOF TOP UNIT | 10.3923 | 600/3 | MDP | MC | 10 | 15 | (3)#12,#12G 1/2"C | (TYPICAL) | 208/3 | 360.2666 | 3
RTU-6 (6 TONS) | ROOF TOP UNIT | 12.4708 | 600/3 | MDP | MC | 12 | 15 | (3)#12,#12G 1/2"C | (TYPICAL) | 240/1 | 240 | 3
RTU-7 (7.5 TONS) | ROOF TOP UNIT | 17.6669 | 600/3 | MDP | MC | 17 | 20 | (3)#12,#12G 1/2"C | (TYPICAL) | 277/1 | 277 | 3
RTU-8 (5 TONS) | ROOF TOP UNIT | 12.4708 | 600/3 | MDP | MC | 12 | 15 | (3)#12,#12G 1/2"C | (TYPICAL) | 277/1/3 | 479.7781 | 3
RTU 9 | ROOF TOP UNIT | 11.6394 | 480/3 | MDP | MC | 14 | 15 | (3)#12,#12G 1/2"C | (TYPICAL) | 277/1 | 277 | 1
WH-1 | WATER HEATER | 12.4708 | 600/3 | HA | EC | 12 | 15 | (3)#12,#12G 1/2"C | SEE 2/E2.1 | 600/1 | 600 | 3
WH-2 | WATER HEATER | 12.4708 | 600/3 | HA | EC | 12 | 15 | (3)#12,#12G 1/2"C | SEE 2/E2.1 | 600/3 | 1039.2305 | 3
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  | 120/208/1 | 208 | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  | 120/208/3 | 360 | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
|  | input mca & v/ph | [5 empty] | input mocp & v/ph |  |  |  | 1
FILENAME: |  | PS 14K_CS_2025_Plumbing Schedule.xlsx

## MDP
NOTES | MOUNT: |  | PWRPLUS |  | 347/600 |  | 3-PHASE, 4W | PANEL |  |  | MDP |  | CAPACITY: | 400 |  | INT CAP: |  | 50 |  | NOTES | [5 empty] | VOLTS | LUGS | MOUNTING
| LOCATION: |  | RECEIVING 117 |  |  |  |  | LUGS: |  | MCB |  |  | DEMAND LOAD: | 181.5473 |  | AV. FAULT: |  | 29.2385 | [7 empty] | 120/208 | MLO | SURFACE
| CKT | LTG | REC | HVAC | MISC | NP | DESCRIPTION | AMP | POLE | F | AMP | POLE | DESCRIPTION | LTG | REC | HVAC | MISC | NP | CKT | [6 empty] | 347/600 | MCB | PWRPLUS
H | 1 |  |  | 4.2 |  |  | RTU-1 (6 TONS) | 15 | 3 | A | 15 | 3 | RTU-2 (4 TONS) |  |  | 3.4641 |  |  | 2 | H | [5 empty] | 120/240 | SFL
|  |  |  | 4.2 | [5 empty] | B | [5 empty] | 3.4641 | [10 empty] | FTL
|  |  |  | 4.2 | [5 empty] | C | [5 empty] | 3.4641
H | 3 |  |  | 3.5 |  |  | RTU-3 (5 TONS) | 15 | 3 | A | 20 | 3 | RTU-4 (7.5 TONS) |  |  | 5.889 |  |  | 4 | H
|  |  |  | 3.5 | [5 empty] | B | [5 empty] | 5.889
|  |  |  | 3.5 | [5 empty] | C | [5 empty] | 5.889
H | 5 |  |  | 4.2 |  |  | RTU-5 (6 TONS) | 15 | 3 | A | 20 | 3 | RTU-6 (7.5 TONS) |  |  | 5.9 |  |  | 6 | H
|  |  |  | 4.2 | [5 empty] | B | [5 empty] | 5.9
|  |  |  | 4.2 | [5 empty] | C | [5 empty] | 5.9
H | 7 |  |  | 5.889 |  |  | RTU-7 (7.5 TONS) | 20 | 3 | A | 15 | 3 | RTU-8 (5 TONS) |  |  | 4.1569 |  |  | 8 | H
|  |  |  | 5.889 | [5 empty] | B | [5 empty] | 4.1569
|  |  |  | 5.889 | [5 empty] | C | [5 empty] | 4.1569
| 9 |  |  | 4.2 |  |  | WH-1 | 15 | 3 | A | 15 | 3 | WH-2 |  |  | 4.2 |  |  | 10
|  |  |  | 4.2 | [5 empty] | B | [5 empty] | 4.2
|  |  |  | 4.2 | [5 empty] | C | [5 empty] | 4.2
| 11 |  |  |  | 0.7 |  | DOCK LEVELLER | 15 | 3 | A | 15 | 3 | SPARE | [5 empty] | 12
[5 empty] | 0.7 |  |  |  |  | B
[5 empty] | 0.7 |  |  |  |  | C
| 13 | 3.86 | 17.33 | 2.12 | 6.4 | 1.5 | XFMR: T1 | 200 | 3 | A | 15 | 3 | VERIS WATT TRANSDUCER (VWT)/ PHASE LOSS MON (PLM) | [5 empty] | 14
|  | 5.34 | 20.98 | 1.97 | 7.36 | 1.5 | 150 |  |  | B
|  | 5.4 | 17.17 | 0 | 9.11 | 3 | 103.04 |  |  | C
| 15 | [5 empty] | SPACE |  | 3 |  |  | 3 | SPACE | [5 empty] | 16
| 17 | [5 empty] | 400A FRAME MOBILE GEN BREAKER W/ MECH INTERLOCK & AUX. SW | 400 | 3 | A |  | 3 | DEDICATED SPACE | [5 empty] | 18
B
C
| 19 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 20
[7 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE
[7 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE
| 21 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 22
[7 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE
[7 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE
| 2 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 2
| 4 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 4
| 6 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 6
| 8 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 8
| 10 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 10
| 12 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 12
| 14 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 14
| 16 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 16
| 18 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 18
| 20 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 20
| 22 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 22
| 24 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 24
| 26 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 26
| 28 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 28
| 30 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 30
| 32 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 32
| 34 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 34
| 36 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 36
| 38 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 38
| 40 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 40
| 42 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 42
| 44 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 44
| 46 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 46
| 48 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 48
| 50 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 50
| 52 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 52
| 54 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 54
| 56 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 56
| 58 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 58
| 60 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 60
| 62 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 62
| 64 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 64
| 66 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 66
| PHASE BALANCE |  |  |  | LOAD TYPE |  | CONNECTED | DEMAND |  |  |  | DEMAND FORMULA |  |  |  | TOTAL LOAD | [5 empty] | DO NOT PLOT
[5 empty] | LIGHTING |  | 14.6 | 18.25 |  |  |  | LOAD X 125% CEC 8-104 CONTINUOUS |  |  |  | CONNECTED |  | DEMAND |  |  |  | LEFT SIDE SUMMARY | [5 empty] | RIGHT SIDE SUMMARY
| F | LOAD |  | % | RECEPTACLE |  | 55.48 | 32.74 |  |  |  | 10KVA + 50% REMAINDER |  |  |  | 241.9369 |  | 188.6695 |  |  |  | LTG | REC | HVAC | MISC | NP |  | LTG | REC | HVAC | MISC | NP
| A | 77.509 |  | 32.04% | HVAC |  | 140.8869 | 112.7095 |  |  |  | LOAD X 80% (USED MCA IN CALCULATION) |  |  |  | 232.8039 |  | 181.5473 |  |  |  | 3.86 | 17.33 | 24.109 | 7.1 | 1.5 | A | 0 | 0 | 23.61 | 0 | 0
| B | 83.449 |  | 34.49% | MISC |  | 24.97 | 24.97 |  |  |  | LOAD X 100% CEC 8-104 NON-CONT. |  |  |  | FILENAME: | [5 empty] | 5.34 | 20.98 | 23.959 | 8.06 | 1.5 | B | 0 | 0 | 23.61 | 0 | 0
| C | 80.979 |  | 33.47% | NP |  | 6 | 0 |  |  |  | 0 NONCOINCIDENTAL LOADS |  |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx | [5 empty] | 5.4 | 17.17 | 21.989 | 9.81 | 3 | C | 0 | 0 | 23.61 | 0 | 0
| REQUIRED FEATURES: A. ALUMINUM BUSSING, COPPER GROUND B. SERVICE ENTRANCE RATED C. MCB TO BE PROVIDED WITH MECHANICAL KIRK-KEY INTERLOCKED WITH MOBILE GENERATOR. D. BREAKERS FOR RTU'S ARE TO BE 'HACR' RATED. | [20 empty] | TOTALS
[22 empty] | LTG | REC | HVAC | MISC | NP
[21 empty] | Z76-> | 3.86 | 17.33 | 47.719 | 7.1 | 1.5 | A
[22 empty] | 5.34 | 20.98 | 47.569 | 8.06 | 1.5 | B
[22 empty] | 5.4 | 17.17 | 45.599 | 9.81 | 3 | C
30P
42P
84P
24P
60P
126P
CNTL ON
CNTL OFF

## LDP
NOTES | MOUNT: |  | PWRPLUS |  | 120/208 |  | 3-PHASE, 4W | PANEL |  |  | LDP |  | CAPACITY: | 600A RATED |  | INT CAP: |  | 22 |  | NOTES | [5 empty] | VOLTS | LUGS | MOUNTING
| LOCATION: |  | RECEIVING 117 |  |  |  |  | LUGS: |  | MLO |  |  | DEMAND LOAD: | 214.097 |  | AV. FAULT: |  | 10.6932 | [7 empty] | 120/208 | MLO | SURFACE
| CKT | LTG | REC | HVAC | MISC | NP | DESCRIPTION | AMP | POLE | F | AMP | POLE | DESCRIPTION | LTG | REC | HVAC | MISC | NP | CKT | [6 empty] | 347/600 | MCB | PWRPLUS
| 1 | 3.86 | 1.39 | 0 | 4 | 0 | PANEL 'LA' | 150 | 3 | A | 100 | 3 | PANEL 'LB' | 0 | 5.3 | 0.85 | 0 | 0 | 2 | [6 empty] | 120/240 | SFL
|  | 5.34 | 0.99 | 1.97 | 2.81 | 0 |  |  |  | B |  |  |  | 0 | 4.86 | 0 | 2.15 | 0 | [8 empty] | FTL
|  | 5.4 | 1.65 | 0 | 5.26 | 0 |  |  |  | C |  |  |  | 0 | 6.62 | 0 | 0.35 | 0
| 3 | 0 | 7.21 | 0 | 0 | 0 | PANEL 'GA' | 150 | 3 | A | 150 | 3 | PANEL 'FC' | 0 | 3.43 | 1.27 | 2.4 | 1.5 | 4
|  | 0 | 9.77 | 0 | 0 | 0 |  |  |  | B |  |  |  | 0 | 5.36 | 0 | 2.4 | 1.5
|  | 0 | 3.18 | 0 | 1.1 | 0 |  |  |  | C |  |  |  | 0 | 5.72 | 0 | 2.4 | 3
| 5 | [5 empty] | SPACE |  | 3 | A | 3 |  | SPACE | [5 empty] | 6
B
C
| 7 | [5 empty] | SPACE |  | 3 | A | 3 |  | SPACE | [5 empty] | 8
B
C
| 9 | [5 empty] | SPACE |  | 3 | A | 3 |  | SPACE | [5 empty] | 10
B
C
| 11 | [5 empty] | SPACE |  | 3 | A | 3 |  | SPACE | [5 empty] | 12
B
C
| 2 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 2
[7 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE
[7 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE
| 4 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 4
[7 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE
[7 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE
| 2 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 2
| 4 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 4
| 6 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 6
| 8 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 8
| 10 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 10
| 12 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 12
| 14 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 14
| 16 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 16
| 18 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 18
| 20 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 20
| 22 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 22
| 24 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 24
| 26 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 26
| 28 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 28
| 30 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 30
| 32 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 32
| 34 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 34
| 36 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 36
| 38 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 38
| 40 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 40
| 42 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 42
| 44 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 44
| 46 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 46
| 48 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 48
| 50 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 50
| 52 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 52
| 54 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 54
| 56 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 56
| 58 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 58
| 60 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 60
| 62 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 62
| 64 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 64
| 66 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 66
| PHASE BALANCE |  |  |  | LOAD TYPE |  | CONNECTED | DEMAND |  |  |  | DEMAND FORMULA |  |  |  | TOTAL LOAD | [5 empty] | DO NOT PLOT
[5 empty] | LIGHTING |  | 14.6 | 18.25 |  |  |  | LOAD X 125% CEC 8-104 CONTINUOUS |  |  |  | CONNECTED |  | DEMAND |  |  |  | LEFT SIDE SUMMARY | [5 empty] | RIGHT SIDE SUMMARY
| F | LOAD |  | % | RECEPTACLE |  | 55.48 | 32.74 |  |  |  | 10KVA + 50% REMAINDER |  |  |  | 103.04 |  | 77.132 |  |  |  | LTG | REC | HVAC | MISC | NP |  | LTG | REC | HVAC | MISC | NP
| A | 31.21 |  | 30.29% | HVAC |  | 4.09 | 3.272 |  |  |  | LOAD X 80% (USED MCA IN CALCULATION) |  |  |  | 286.0104 |  | 214.097 |  |  |  | 3.86 | 8.6 | 0 | 4 | 0 | A | 0 | 8.73 | 2.12 | 2.4 | 1.5
| B | 37.15 |  | 36.05% | MISC |  | 22.87 | 22.87 |  |  |  | LOAD X 100% CEC 8-104 NON-CONT. |  |  |  | FILENAME: | [5 empty] | 5.34 | 10.76 | 1.97 | 2.81 | 0 | B | 0 | 10.22 | 0 | 4.55 | 1.5
| C | 34.68 |  | 33.66% | NP |  | 6 | 0 |  |  |  | 0 NONCOINCIDENTAL LOADS |  |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx | [5 empty] | 5.4 | 4.83 | 0 | 6.36 | 0 | C | 0 | 12.34 | 0 | 2.75 | 3
| REQUIRED FEATURES: A. ALUMINUM BUSSING, COPPER GROUND | [20 empty] | TOTALS
[22 empty] | LTG | REC | HVAC | MISC | NP
[21 empty] | Z76-> | 3.86 | 17.33 | 2.12 | 6.4 | 1.5 | A
[22 empty] | 5.34 | 20.98 | 1.97 | 7.36 | 1.5 | B
[22 empty] | 5.4 | 17.17 | 0 | 9.11 | 3 | C
30P
42P
84P
24P
60P
126P
CNTL ON
CNTL OFF

## FC
NOTES | MOUNT: |  | FLUSH |  | 120/208 |  | 3-PHASE, 4W | PANEL |  |  | FC |  | CAPACITY: | 225A |  | INT CAP: |  | 14 |  | NOTES | [5 empty] | VOLTS | LUGS | MOUNTING
| LOCATION: |  | HOLDING ROOM 122 |  |  |  |  | LUGS: |  | MLO |  |  | DEMAND LOAD: | 56.8218 |  | AV. FAULT: |  | 10.6932 | [7 empty] | 120/208 | MLO | SURFACE
| CKT | LTG | REC | HVAC | MISC | NP | DESCRIPTION | AMP | POLE | F | AMP | POLE | DESCRIPTION | LTG | REC | HVAC | MISC | NP | CKT | [6 empty] | 277/480 | MCB | FLUSH
G | 1 |  | 0.54 |  |  |  | REC FISH PREP | 20 | 1 | A | 15 | 1 | EXHAUST FAN EF-3 (.20 BHP) |  |  | 0.87 |  |  | 2 | C | [5 empty] | 120/240 | SFL
| 3 |  |  |  | 0.8 |  | POWER DROP #5 - SM. ANIMAL | 20 | 1 | B | 20 | 1 | POWER DROP #2 - LG. AQUA. |  |  |  | 0.8 |  | 4 | [7 empty] | FTL
| 5 |  |  |  |  | 1.5 | EUH-1 | 20 | 2 | C | 20 | 1 | POWER DROP #1 - BETTA |  |  |  | 0.8 |  | 6
| 7 |  |  |  |  | 1.5 |  |  |  | A | 20 | 1 | POWER DROP #3 - SHO3 |  |  |  | 0.8 |  | 8
| 9 |  |  |  |  | 1.5 | EUH-2 | 20 | 2 | B | 20 | 1 | POWER DROP #4 - REP. FEED. |  |  |  | 0.8 |  | 10
| 11 |  |  |  |  | 1.5 |  |  |  | C | 20 | 1 | POWER DROP #3 - PLANT |  |  |  | 0.8 |  | 12
| 13 |  |  |  | 0.8 |  | POWER DROP #4 - REPTILE | 20 | 1 | A | 20 | 1 | POWER DROP #2 - LG. AQUA. |  |  |  | 0.8 |  | 14
G | 15 |  | 0.54 |  |  |  | FISH AREA FREEZER | 20 | 1 | B | 20 | 1 | ASSOC. RES. - VENDING |  | 1 |  |  |  | 16
| 17 |  |  |  | 0.8 |  | POWER DROP #6 - BIRD | 20 | 1 | C | 20 | 1 | ASSOC. RES. - VENDING |  | 1 |  |  |  | 18
| 19 |  |  | 0.4 |  |  | MORORIZED DAMPER #1 & #2 | 20 | 1 | A | 20 | 1 | ASSOC. RES. - FRIDGE |  | 0.57 |  |  |  | 20 | G
G | 21 |  | 0.72 |  |  |  | HOLDING RM. #1 GFI RECEPT. | 20 | 1 | B | 20 | 1 | ASSOC. RES. - COUNT. RECEPT. |  | 0.54 |  |  |  | 22 | G
G | 23 |  | 0.72 |  |  |  | HOLDING RM. #2 GFI RECEPT. | 20 | 1 | C | 20 | 1 | ASSOC. RES. - MICROWAVE |  | 1.3 |  |  |  | 24
G | 25 |  | 0.4 |  |  |  | RECEPT. FISH EQUIP. | 20 | 1 | A | 20 | 1 | ASSOC. RES. RECEPT. |  | 0.3 |  |  |  | 26
G | 27 |  | 0.54 |  |  |  | FISH PREP. FRIDGE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 28
G | 29 |  | 0.54 |  |  |  | TURTLE TANK RECEPT. | 20 | 1 | C | 20 | 1 | FISH FILTRATION RECEPT. |  | 0.54 |  |  |  | 30 | G
G | 31 |  | 0.54 |  |  |  | ADOPTIONS GFI RECEPT. | 20 | 1 | A | 20 | 1 | FISH FILTRATION RECEPT. |  | 0.54 |  |  |  | 32 | G
| 33 |  | 0.54 |  |  |  | RECEPT. - ADOPTIONS | 20 | 1 | B | 20 | 1 | FISH FILTRATION RECEPT. |  | 0.54 |  |  |  | 34 | G
| 35 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | FISH FILTRATION RECEPT. |  | 0.54 |  |  |  | 36 | G
| 37 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | FISH FILTRATION RECEPT. |  | 0.54 |  |  |  | 38 | G
G | 39 |  | 0.4 |  |  |  | RTU RECEPT. (GFI/WP) | 20 | 1 | B | 20 | 1 | FISH FILTRATION RECEPT. |  | 0.54 |  |  |  | 40 | G
| 41 |  | 0.54 |  |  |  | COLUMN RECEPT. - SALES | 20 | 1 | C | 20 | 1 | FISH FILTRATION RECEPT. |  | 0.54 |  |  |  | 42 | G
| 43 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 44
| 45 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 46
| 47 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 48
| 49 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 50
| 51 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 52
| 53 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 54
| 55 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 56
| 57 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 58
| 59 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 60
| 61 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 62
| 63 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 64
| 65 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 66
| 67 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 68
| 69 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 70
| 71 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 72
| 73 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 74
| 75 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 76
| 77 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 78
| 79 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 80
| 81 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 82
| 83 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 84
| 85 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 86
| 87 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 88
| 89 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 90
| 91 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 92
| 93 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 94
| 95 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 96
| 97 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 98
| 99 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 100
| 101 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 102
| 103 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 104
| 105 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 106
| 107 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 108
| 109 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 110
| 111 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 112
| 113 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 114
| 115 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 116
| 117 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 118
| 119 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 120
| 121 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 122
| 123 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 124
| 125 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 126
| PHASE BALANCE |  |  |  | LOAD TYPE |  | CONNECTED | DEMAND |  |  |  | DEMAND FORMULA |  |  |  | TOTAL LOAD | [5 empty] | DO NOT PLOT
[5 empty] | LIGHTING |  | 0 | 0 |  |  |  | LOAD X 125% NEC 210.19 CONTINUOUS |  |  |  | CONNECTED |  | DEMAND |  |  |  | LEFT SIDE SUMMARY | [5 empty] | RIGHT SIDE SUMMARY
| F | LOAD |  | % | RECEPTACLE |  | 14.51 | 12.255 |  |  |  | 10KVA + 50% REMAINDER NEC 220.44 |  |  |  | 28.98 |  | 20.471 |  |  |  | LTG | REC | HVAC | MISC | NP |  | LTG | REC | HVAC | MISC | NP
| A | 8.6 |  | 29.68% | HVAC |  | 1.27 | 1.016 |  |  |  | LOAD X 80% (USED MCA IN CALCULATION) |  |  |  | 80.4404 |  | 56.8218 |  |  |  | 0 | 1.48 | 0.4 | 0.8 | 1.5 | A | 0 | 1.95 | 0.87 | 1.6 | 0
| B | 9.26 |  | 31.95% | MISC |  | 7.2 | 7.2 |  |  |  | LOAD X 100% NEC 210.19 NON-CONT. |  |  |  | FILENAME: | [5 empty] | 0 | 2.74 | 0 | 0.8 | 1.5 | B | 0 | 2.62 | 0 | 1.6 | 0
| C | 11.12 |  | 38.37% | NP |  | 6 | 0 |  |  |  | 0 NONCOINCIDENTAL LOADS NEC 220.60 |  |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx | [5 empty] | 0 | 1.8 | 0 | 0.8 | 3 | C | 0 | 3.92 | 0 | 1.6 | 0
| REQUIRED FEATURES: A. ALUMINUM BUSSING, COPPER GROUND B. PROVIDE WITH ISOLATED GROUND BUS | [20 empty] | TOTALS
[22 empty] | LTG | REC | HVAC | MISC | NP
[21 empty] | Z76-> | 0 | 3.43 | 1.27 | 2.4 | 1.5 | A
[22 empty] | 0 | 5.36 | 0 | 2.4 | 1.5 | B
[22 empty] | 0 | 5.72 | 0 | 2.4 | 3 | C
Mike F. Info Only
[5 empty] | Watts | Amp | KVA
[5 empty] | 120 | 1 | 0.12
[5 empty] | 360 | 3 | 0.36
[5 empty] | 600 | 5 | 0.6
[5 empty] | 840 | 7 | 0.84
[5 empty] | 1080 | 9 | 1.08
[5 empty] | 1320 | 11 | 1.32
[5 empty] | 1560 | 13 | 1.56
[5 empty] | 1800 | 15 | 1.8
30P
42P
84P
24P
60P
126P
CNTL ON
CNTL OFF

## GA
NOTES | MOUNT: |  | FLUSH |  | 120/208 |  | 3-PHASE, 4W | PANEL |  |  | GA |  | CAPACITY: | 225A |  | INT CAP: |  | 14 |  | NOTES | [5 empty] | VOLTS | LUGS | MOUNTING
| LOCATION: |  | DRYING AREA 115 |  |  |  |  | LUGS: |  | MLO |  |  | DEMAND LOAD: | 44.9112 |  | AV. FAULT: |  | 10.6932 | [7 empty] | 120/208 | MLO | SURFACE
| CKT | LTG | REC | HVAC | MISC | NP | DESCRIPTION | AMP | POLE | F | AMP | POLE | DESCRIPTION | LTG | REC | HVAC | MISC | NP | CKT | [6 empty] | 277/480 | MCB | FLUSH
G | 1 |  | 1.26 |  |  |  | DRYER RECEPT. | 15 | 1 | A | 20 | 1 | SALON RECEPT. |  | 0.84 |  |  |  | 2 | G | [5 empty] | 120/240 | SFL
G | 3 |  | 1.26 |  |  |  | DRYER RECEPT. | 15 | 1 | B | 20 | 1 | SALON RECEPT. |  | 0.84 |  |  |  | 4 | G | [6 empty] | FTL
G | 5 |  | 1.26 |  |  |  | DRYER RECEPT. | 15 | 1 | C | 20 | 1 | SALON RECEPT. |  | 0.84 |  |  |  | 6 | G
G | 7 |  | 1.26 |  |  |  | DRYER RECEPT. | 15 | 1 | A | 20 | 1 | SALON RECEPT. |  | 0.84 |  |  |  | 8 | G
G | 9 |  | 1.26 |  |  |  | DRYER RECEPT. | 15 | 1 | B | 20 | 1 | SPARE | [5 empty] | 10
G | 11 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 12
| 13 |  | 0.36 |  |  |  | BUZZER | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 14
G | 15 |  | 1.26 |  |  |  | MOBILE DRYER RECEPT. | 20 | 1 | B | 20 | 1 | MOBILE DRYER RECEPT. |  | 1.26 |  |  |  | 16 | G
| 17 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 18
G | 19 |  | 1.26 |  |  |  | MASTER BLASTER RECEPT. | 30 | 1 | A | 20 | 1 | SPARE | [5 empty] | 20
G | 21 |  | 1.26 |  |  |  | MASTER BLASTER RECEPT. | 30 | 1 | B | 20 | 1 | SALON CHECK-IN I.G. RECEPT. |  | 0.54 |  |  |  | 22 | L
| 23 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SALON CHECK-IN I.G. RECEPT. |  | 0.54 |  |  |  | 24 | L
| 25 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SALON CHECK-IN I.G. RECEPT. |  | 0.54 |  |  |  | 26 | L
| 27 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SALON CHECK-IN RECEPT. |  | 0.54 |  |  |  | 28
| 29 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SALON CHECK-IN RECEPT. |  | 0.54 |  |  |  | 30
| 31 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 32
| 33 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | HALLWAY RECEPT. |  | 0.3 |  |  |  | 34
| 35 | [5 empty] | SPARE | 20 | 1 | C | 15 | 1 | WASH. DOOR OPER. & CALL SYS. |  |  |  | 1.1 |  | 36
| 37 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | WASHROOM GFI RECEPT. |  | 0.85 |  |  |  | 38 | G
G | 39 |  | 0.4 |  |  |  | RTU RECEPT. (GFI/WP) | 20 | 1 | B | 20 | 1 | DRINKING FOUNTAIN: EWC-1 |  | 0.85 |  |  |  | 40 | G
| 41 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 42
| 43 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 44
| 45 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 46
| 47 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 48
| 49 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 50
| 51 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 52
| 53 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 54
| 55 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 56
| 57 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 58
| 59 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 60
| 61 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 62
| 63 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 64
| 65 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 66
| 67 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 68
| 69 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 70
| 71 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 72
| 73 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 74
| 75 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 76
| 77 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 78
| 79 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 80
| 81 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 82
| 83 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 84
| 85 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 86
| 87 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 88
| 89 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 90
| 91 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 92
| 93 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 94
| 95 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 96
| 97 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 98
| 99 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 100
| 101 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 102
| 103 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 104
| 105 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 106
| 107 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 108
| 109 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 110
| 111 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 112
| 113 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 114
| 115 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 116
| 117 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 118
| 119 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 120
| 121 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 122
| 123 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 124
| 125 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 126
| PHASE BALANCE |  |  |  | LOAD TYPE |  | CONNECTED | DEMAND |  |  |  | DEMAND FORMULA |  |  |  | TOTAL LOAD | [5 empty] | DO NOT PLOT
[5 empty] | LIGHTING |  | 0 | 0 |  |  |  | LOAD X 125% NEC 210.19 CONTINUOUS |  |  |  | CONNECTED |  | DEMAND |  |  |  | LEFT SIDE SUMMARY | [5 empty] | RIGHT SIDE SUMMARY
| F | LOAD |  | % | RECEPTACLE |  | 20.16 | 15.08 |  |  |  | 10KVA + 50% REMAINDER NEC 220.44 |  |  |  | 21.26 |  | 16.18 |  |  |  | LTG | REC | HVAC | MISC | NP |  | LTG | REC | HVAC | MISC | NP
| A | 7.21 |  | 33.91% | HVAC |  | 0 | 0 |  |  |  | LOAD X 80% (USED MCA IN CALCULATION) |  |  |  | 59.0119 |  | 44.9112 |  |  |  | 0 | 4.14 | 0 | 0 | 0 | A | 0 | 3.07 | 0 | 0 | 0
| B | 9.77 |  | 45.95% | MISC |  | 1.1 | 1.1 |  |  |  | LOAD X 100% NEC 210.19 NON-CONT. |  |  |  | FILENAME: | [5 empty] | 0 | 5.44 | 0 | 0 | 0 | B | 0 | 4.33 | 0 | 0 | 0
| C | 4.28 |  | 20.13% | NP |  | 0 | 0 |  |  |  | 0 NONCOINCIDENTAL LOADS NEC 220.60 |  |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx | [5 empty] | 0 | 1.26 | 0 | 0 | 0 | C | 0 | 1.92 | 0 | 1.1 | 0
| REQUIRED FEATURES: A. ALUMINUM BUSSING, COPPER GROUND B. PROVIDE WITH ISOLATED GROUND BUS | [20 empty] | TOTALS
[22 empty] | LTG | REC | HVAC | MISC | NP
[21 empty] | Z76-> | 0 | 7.21 | 0 | 0 | 0 | A
[22 empty] | 0 | 9.77 | 0 | 0 | 0 | B
[22 empty] | 0 | 3.18 | 0 | 1.1 | 0 | C
Mike F. Info Only
[5 empty] | Watts | Amp | KVA
[5 empty] | 120 | 1 | 0.12
[5 empty] | 360 | 3 | 0.36
[5 empty] | 600 | 5 | 0.6
[5 empty] | 840 | 7 | 0.84
[5 empty] | 1080 | 9 | 1.08
[5 empty] | 1320 | 11 | 1.32
[5 empty] | 1560 | 13 | 1.56
[5 empty] | 1800 | 15 | 1.8
30P
42P
84P
24P
60P
126P
CNTL ON
CNTL OFF

## LA
NOTES | MOUNT: |  | PWRPLUS |  | 120/208 |  | 3-PHASE, 4W | PANEL |  |  | LA |  | CAPACITY: | 225 |  | INT CAP: |  | 14 |  | NOTES | [5 empty] | VOLTS | LUGS | MOUNTING
| LOCATION: |  | RECEIVING AREA 117 |  |  |  |  | LUGS: |  | MLO |  |  | DEMAND LOAD: | 99.7206 |  | AV. FAULT: |  | 10.6932 | [7 empty] | 120/208 | MLO | SURFACE
| CKT | LTG | REC | HVAC | MISC | NP | DESCRIPTION | AMP | POLE | F | AMP | POLE | DESCRIPTION | LTG | REC | HVAC | MISC | NP | CKT | [6 empty] | 277/480 | MCB | PWRPLUS
C | 1 |  | 0.85 |  |  |  | AQUARIUM | 20 | 1 | A | 20 | 1 | SPRINKLER ALARM |  |  |  | 0.35 |  | 2 | L | [5 empty] | 120/240 | SFL
C | 3 |  |  | 0.87 |  |  | EXHAUST FAN EF-4 (.06 BHP) | 15 | 1 | B | 20 | 1 | EXHAUST FAN EF-2 (.46 BHP) |  |  | 1.1 |  |  | 4 | C | [6 empty] | FTL
| 5 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPRINKLER BELL RISER |  |  |  | 0.35 |  | 6 | L
| 7 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 8
| 9 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | RECIRC. PUMP RP-1 |  |  |  | 0.85 |  | 10
| 11 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SCRUBBER |  | 0.85 |  |  |  | 12 | G
C/G | 13 | 0.8 |  |  |  |  | SPECIALTY AREA LIGHTING | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 14
L | 15 |  |  |  | 0.36 |  | CP-1 EMS ELECTRONICS | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 16
L | 17 |  |  |  | 0.36 |  | CP-1 EMS OUTPUTS | 20 | 1 | C | 20 | 1 | CONTACTOR COILS |  | 0.35 |  |  |  | 18 | L
G | 19 |  | 0.54 |  |  |  | EXTERIOR RECEPTACLE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 20
| 21 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | FRONT SIGN (GROOMING ETC.) |  | 0.54 |  |  |  | 22 | C
C | 23 |  |  |  | 0.9 |  | FRONT SIGNAGE (PETSMART) | 20 | 1 | C | 30 | 2 | BATTERY CHARGER |  |  |  | 2.4 |  | 24
C | 25 |  |  |  | 0.9 |  | SIDE SIGNAGE (PETSMART | 20 | 1 | A | [6 empty] | 2.4 |  | 26
C | 27 |  |  |  | 0.9 |  | SIDE SIGNAGE (PETSMART | 20 | 1 | B | 20 | 1 | DOOR HORN |  |  |  | 0.35 |  | 28
C | 29 |  |  |  | 0.9 |  | REAR SIGNAGE (PETSMART | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 30
| 31 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 32
C | 33 | 0.84 |  |  |  |  | LIGHTS - NIGHT LIGHTS | 20 | 1 | B | 20 | 1 | RECEPTACLE - TMB |  | 0.45 |  |  |  | 34 | L
C | 35 | 1.6 |  |  |  |  | LIGHTING - SALES | 20 | 1 | C | 20 | 1 | RECEPTACLE - TMB |  | 0.45 |  |  |  | 36 | L
C | 37 | 1.1 |  |  |  |  | LIGHTING - SALES | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 38
C | 39 | 1.1 |  |  |  |  | LIGHTING - SALES | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 40
C | 41 | 1.6 |  |  |  |  | LIGHTING - SALES | 20 | 1 | C | 15 | 2 | BOOSTER PUMP DBP-1 | [5 empty] | 42 | G
C | 43 | 1.6 |  |  |  |  | LIGHTING - SALES | 20 | 1 | A | [8 empty] | 44
C | 45 | 1.6 |  |  |  |  | LIGHTING - SALES | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 46
| 47 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 48
| 49 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | EXTERIOR WALL PACKS |  |  |  | 0.35 |  | 50 | C
C | 51 | 1.1 |  |  |  |  | LIGHTS - SALON/BATHING/WASHROOMS | 20 | 1 | B | 20 | 1 | EXTERIOR WALL PACKS |  |  |  | 0.35 |  | 52 | C
C | 53 | 0.6 |  |  |  |  | LIGHTING - RECEIVING | 20 | 1 | C | 20 | 1 | EXTERIOR CANOPY LIGHTING |  |  |  | 0.35 |  | 54 | C
C | 55 | 0.36 |  |  |  |  | LIGHTS - OFFICE/STAFF | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 56
C | 57 | 0.7 |  |  |  |  | LIGHTING - FISH/ADOPTION | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 58
L/* | 59 | 1.6 |  |  |  |  | LIGHTING - EMERG./EXIT | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 60
| 61 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 62
| 63 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 64
| 65 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 66
| 67 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 68
| 69 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 70
| 71 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 72
| 73 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 74
| 75 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 76
| 77 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 78
| 79 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 80
| 81 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 82
| 83 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 84
| 85 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 86
| 87 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 88
| 89 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 90
| 91 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 92
| 93 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 94
| 95 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 96
| 97 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 98
| 99 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 100
| 101 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 102
| 103 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 104
| 105 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 106
| 107 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 108
| 109 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 110
| 111 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 112
| 113 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 114
| 115 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 116
| 117 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 118
| 119 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 120
| 121 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 122
| 123 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 124
| 125 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 126
| PHASE BALANCE |  |  |  | LOAD TYPE |  | CONNECTED | DEMAND |  |  |  | DEMAND FORMULA |  |  |  | TOTAL LOAD | [5 empty] | DO NOT PLOT
[5 empty] | LIGHTING |  | 14.6 | 18.25 |  |  |  | LOAD X 125% NEC 210.19 CONTINUOUS |  |  |  | CONNECTED |  | DEMAND |  |  |  | LEFT SIDE SUMMARY | [5 empty] | RIGHT SIDE SUMMARY
| F | LOAD |  | % | RECEPTACLE |  | 4.03 | 4.03 |  |  |  | 10KVA + 50% REMAINDER NEC 220.44 |  |  |  | 32.67 |  | 35.926 |  |  |  | LTG | REC | HVAC | MISC | NP |  | LTG | REC | HVAC | MISC | NP
| A | 9.25 |  | 28.31% | HVAC |  | 1.97 | 1.576 |  |  |  | LOAD X 80% (USED MCA IN CALCULATION) |  |  |  | 90.6829 |  | 99.7206 |  |  |  | 3.86 | 1.39 | 0 | 0.9 | 0 | A | 0 | 0 | 0 | 3.1 | 0
| B | 11.11 |  | 34.01% | MISC |  | 12.07 | 12.07 |  |  |  | LOAD X 100% NEC 210.19 NON-CONT. |  |  |  | FILENAME: | [5 empty] | 5.34 | 0 | 0.87 | 1.26 | 0 | B | 0 | 0.99 | 1.1 | 1.55 | 0
| C | 12.31 |  | 37.68% | NP |  | 0 | 0 |  |  |  | 0 NONCOINCIDENTAL LOADS NEC 220.60 |  |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx | [5 empty] | 5.4 | 0 | 0 | 2.16 | 0 | C | 0 | 1.65 | 0 | 3.1 | 0
| REQUIRED FEATURES: A. ALUMINUM BUSSING, COPPER GROUND B. PROVIDE WITH ISOLATED GROUND BUS | [20 empty] | TOTALS
[22 empty] | LTG | REC | HVAC | MISC | NP
[21 empty] | Z76-> | 3.86 | 1.39 | 0 | 4 | 0 | A
[22 empty] | 5.34 | 0.99 | 1.97 | 2.81 | 0 | B
[22 empty] | 5.4 | 1.65 | 0 | 5.26 | 0 | C
Mike F. Info Only
[5 empty] | Watts | Amp | KVA
[5 empty] | 120 | 1 | 0.12
[5 empty] | 360 | 3 | 0.36
[5 empty] | 600 | 5 | 0.6
[5 empty] | 840 | 7 | 0.84
[5 empty] | 1080 | 9 | 1.08
[5 empty] | 1320 | 11 | 1.32
[5 empty] | 1560 | 13 | 1.56
[5 empty] | 1800 | 15 | 1.8
30P
42P
84P
24P
60P
126P
CNTL ON
CNTL OFF

## TRANSFORMER (hidden)
TRANSFORMER SCHEDULE:
PLAN MARK | kVA | PHASE | PRI VOLT. | SEC. VOLT | SERVING | COMMENTS
T-1 | 150 | 3 Ø | 480 | 120/208 | LA & LD | MOUNTED ABOVE POWER WALL BY EC
T-2 | 75 | 3 Ø | 480 | 120/208 | LB & LC | MOUNTED AT DECK ABOVE PANEL LB AND LC BY EC
T-3 | 75 | 3 Ø | 480 | 120/208 | LB & LC | MOUNTED AT DECK ABOVE PANEL LB AND LC BY EC
FILENAME: |  | PS 14K_CS_2025_Plumbing Schedule.xlsx

## CONTACTORS (hidden)
CONTACTORS SCHEDULE:
DESCRIPTION |  | COIL |  |  | CONTROL |  |  | COMMENTS
MARK | AMP / POLES | PNL | CKT | ELEC. HELD | PNL | CKTS | OUTPUT #
C-1 | 150A / 3P | LA | 2 | NO | LD1 | PANEL | 0-2-0-D008 | VALANCE & TRACK LTG.
C-2 | 150A / 3P | LA | 2 | NO | LD2 | PANEL | 0-2-0-D008 | VALANCE & TRACK LTG.
C-3 | 20A / 4P | LA | 2 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D007 | LINEAR SALES LTG.
C-4 | 20A / 4P | LA | 2 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D007 | LINEAR SALES LTG.
C-5 | 20A / 4P | LA | 2 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D007 | LINEAR SALES LTG.
C-6 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D006 | LINEAR SALES LTG. (PERIMETER LTG.)
C-7 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D005 | PRESALES / RECEIVING LTG.
C-8 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D004 | VESTIBULE / CUST. LTG.
C-9 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D008 | PENDANT (3) LAMPS
C-10 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D007 | PENDANT (3) LAMPS
C-11 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D006 | PENDANT (3) LAMPS
C-12 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D005 | PENDANT NL LAMPS
C-13 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D004 | SECURITY LIGHTING
C-14 | 20A / 4P | LA | 4 | YES | HA | SEE DETAIL 2/E302 | 0-2-0-D003 | EXTERIOR LIGHTING
C-15 | 20A / 4P | LA | 4 | YES | L1A | SEE DETAIL 2/E302 | 0-2-0-D002 | TRU EXTERIOR SIGNAGE
C-16 | 20A / 4P | LA | 4 | YES | L1A | SEE DETAIL 2/E302 | 0-2-0-D002 | BRU EXTERIOR SIGNAGE
FILENAME: |  | PS 14K_CS_2025_Plumbing Schedule.xlsx

## LB
NOTES | MOUNT: |  | FLUSH |  | 120/208 |  | 3-PHASE, 4W | PANEL |  |  | LB |  | CAPACITY: | 125 |  | INT CAP: |  | 14 |  | NOTES | [5 empty] | VOLTS | LUGS | MOUNTING
| LOCATION: |  | MANAGER/VAULT RM. 104 |  |  |  |  | LUGS: |  | MLO |  |  | DEMAND LOAD: | 45.9937 |  | AV. FAULT: |  | 10.6932 | [7 empty] | 120/208 | MLO | SURFACE
| CKT | LTG | REC | HVAC | MISC | NP | DESCRIPTION | AMP | POLE | F | AMP | POLE | DESCRIPTION | LTG | REC | HVAC | MISC | NP | CKT | [6 empty] | 277/480 | MCB | FLUSH
G | 1 |  | 0.4 |  |  |  | RTU RECEPT. (GFI/WP) | 20 | 1 | A | 15 | 1 | EXHAUST FAN EF-1 (.07 BHP) |  |  | 0.85 |  |  | 2 | C | [5 empty] | 120/240 | SFL
| 3 |  | 1.1 |  |  |  | NATURAL FREEZER | 20 | 1 | B | 20 | 1 | CHECKSTAND I.G. RECEPT. |  | 0.54 |  |  |  | 4 | L | [6 empty] | FTL
| 5 |  | 1.1 |  |  |  | NATURAL FREEZER | 20 | 1 | C | 20 | 1 | CHECKSTAND I.G. RECEPT. |  | 0.54 |  |  |  | 6 | L
| 7 |  | 1.1 |  |  |  | NATURAL FREEZER | 20 | 1 | A | 20 | 1 | CHECKSTAND I.G. RECEPT. |  | 0.54 |  |  |  | 8 | L
| 9 |  | 1.1 |  |  |  | NATURAL FREEZER | 20 | 1 | B | 20 | 1 | REC CASH WRAP |  | 0.54 |  |  |  | 10
| 11 |  | 1.1 |  |  |  | NATURALCOOLER | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 12
| 13 |  | 1.1 |  |  |  | NATURALCOOLER | 20 | 1 | A | 20 | 1 | TAG MACHINE |  | 0.54 |  |  |  | 14
| 15 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | BIRD DETERRENT |  | 0.5 |  |  |  | 16
| 17 |  | 0.54 |  |  |  | FRONT P.O.S. RECEPT. | 20 | 1 | C | 20 | 1 | MUSAK SYSTEM |  | 0.4 |  |  |  | 18 | L
| 19 |  | 0.54 |  |  |  | BOPIS UNIT - FRONT CASH | 20 | 1 | A | 20 | 1 | COPY/EQUIP I.G. SERVER RACK |  | 0.54 |  |  |  | 20 | L
| 21 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | COPY/EQUIP. I.G. RECEPT. |  | 0.54 |  |  |  | 22
| 23 |  | 0.54 |  |  |  | BOPIS CLOSET RECEPT. | 20 | 1 | C | 20 | 1 | COPY/EQUIP. RECEPT. |  | 0.54 |  |  |  | 24
| 25 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | MANAGERS OFFICE I.G. RECEPT. |  | 0.54 |  |  |  | 26
| 27 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | MANAGERS OFFICE RECEPT. |  | 0.54 |  |  |  | 28
| 29 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 30
| 31 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 32
| 33 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 34
| 35 |  | 0.6 |  |  |  | POWER DROP #7 - FRONT POS | 20 | 1 | C | 20 | 1 | COLUMN RECEPT. - SALES |  | 0.54 |  |  |  | 36
| 37 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 38
| 39 |  |  |  | 1.3 |  | AUTO DOOR | 20 | 1 | B | 20 | 1 | FIRE ALARM (PAINT RED) |  |  |  | 0.85 |  | 40 | L/*
L | 41 |  |  |  | 0.35 |  | FRONT SECURITY RECEPT. | 20 | 1 | C | 20 | 1 | EXTERIOR RECEPT. |  | 0.72 |  |  |  | 42 | G
| 43 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 44
| 45 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 46
| 47 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 48
| 49 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 50
| 51 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 52
| 53 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 54
| 55 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 56
| 57 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 58
| 59 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 60
| 61 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 62
| 63 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 64
| 65 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 66
| 67 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 68
| 69 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 70
| 71 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 72
| 73 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 74
| 75 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 76
| 77 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 78
| 79 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 80
| 81 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 82
| 83 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 84
| 85 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 86
| 87 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 88
| 89 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 90
| 91 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 92
| 93 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 94
| 95 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 96
| 97 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 98
| 99 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 100
| 101 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 102
| 103 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 104
| 105 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 106
| 107 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 108
| 109 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 110
| 111 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 112
| 113 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 114
| 115 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 116
| 117 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 118
| 119 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 120
| 121 | [5 empty] | SPARE | 20 | 1 | A | 20 | 1 | SPARE | [5 empty] | 122
| 123 | [5 empty] | SPARE | 20 | 1 | B | 20 | 1 | SPARE | [5 empty] | 124
| 125 | [5 empty] | SPARE | 20 | 1 | C | 20 | 1 | SPARE | [5 empty] | 126
| PHASE BALANCE |  |  |  | LOAD TYPE |  | CONNECTED | DEMAND |  |  |  | DEMAND FORMULA |  |  |  | TOTAL LOAD | [5 empty] | DO NOT PLOT
[5 empty] | LIGHTING |  | 0 | 0 |  |  |  | LOAD X 125% NEC 210.19 CONTINUOUS |  |  |  | CONNECTED |  | DEMAND |  |  |  | LEFT SIDE SUMMARY | [5 empty] | RIGHT SIDE SUMMARY
| F | LOAD |  | % | RECEPTACLE |  | 16.78 | 13.39 |  |  |  | 10KVA + 50% REMAINDER NEC 220.44 |  |  |  | 20.13 |  | 16.57 |  |  |  | LTG | REC | HVAC | MISC | NP |  | LTG | REC | HVAC | MISC | NP
| A | 6.15 |  | 30.55% | HVAC |  | 0.85 | 0.68 |  |  |  | LOAD X 80% (USED MCA IN CALCULATION) |  |  |  | 55.8753 |  | 45.9937 |  |  |  | 0 | 3.14 | 0 | 0 | 0 | A | 0 | 2.16 | 0.85 | 0 | 0
| B | 7.01 |  | 34.82% | MISC |  | 2.5 | 2.5 |  |  |  | LOAD X 100% NEC 210.19 NON-CONT. |  |  |  | FILENAME: | [5 empty] | 0 | 2.2 | 0 | 1.3 | 0 | B | 0 | 2.66 | 0 | 0.85 | 0
| C | 6.97 |  | 34.62% | NP |  | 0 | 0 |  |  |  | 0 NONCOINCIDENTAL LOADS NEC 220.60 |  |  |  | PS 14K_CS_2025_Plumbing Schedule.xlsx | [5 empty] | 0 | 3.88 | 0 | 0.35 | 0 | C | 0 | 2.74 | 0 | 0 | 0
| REQUIRED FEATURES: A. ALUMINUM BUSSING, COPPER GROUND B. PROVIDE WITH ISOLATED GROUND BUS | [20 empty] | TOTALS
[22 empty] | LTG | REC | HVAC | MISC | NP
[21 empty] | Z76-> | 0 | 5.3 | 0.85 | 0 | 0 | A
[22 empty] | 0 | 4.86 | 0 | 2.15 | 0 | B
[22 empty] | 0 | 6.62 | 0 | 0.35 | 0 | C
Mike F. Info Only
[5 empty] | Watts | Amp | KVA
[5 empty] | 120 | 1 | 0.12
[5 empty] | 360 | 3 | 0.36
[5 empty] | 600 | 5 | 0.6
[5 empty] | 840 | 7 | 0.84
[5 empty] | 1080 | 9 | 1.08
[5 empty] | 1320 | 11 | 1.32
[5 empty] | 1560 | 13 | 1.56
[5 empty] | 1800 | 15 | 1.8
30P
42P
84P
24P
60P
126P
CNTL ON
CNTL OFF

## LOOKUP TABLES
C-VALUES PER COOPER-BUSSMANN SPD ELECTRICAL PROTECTION HANDBOOK TABLE 4
(ASSUMED FEEDER IN PVC, THUS NONMAGNETIC)
WIRE SIZE | 600V-COPPER | 600V-ALUMINUM
14 | 389 | 237
12 | 617 | 376
10 | 981 | 599
8 | 1559 | 952
6 | 2430 | 1482
4 | 3826 | 2350
3 | 4811 | 2961
2 | 6044 | 3730
1 | 7493 | 4678
1/0 | 9317 | 5838
2/0 | 11424 | 7301
3/0 | 13923 | 9110
4/0 | 16673 | 11174
250 | 18594 | 12862
300 | 20686 | 14923
350 | 22737 | 16813
400 | 24297 | 18506
500 | 26706 | 21391
600 | 28033 | 23451
750 | 29735 | 25976
TRANSFORMER SHORT-CIRCUIT TABLE FROM COOPER-BUSSMANN SPD TABLE 1:
(Had to put in descending order of KVA for the Excel function to work properly)
V (L-L) | PH | KVA | FULL LOAD AMPS | %Z | S-C AMPS |  |  | fla/%z | diff
240 | 1 | 167 | 696 | 1.6 | 60225 |  |  | 43500 | -16725
240 | 1 | 100 | 417 | 1.6 | 42478 |  |  | 26062.5 | -16415.5
240 | 1 | 75 | 313 | 1.5 | 32637 |  |  | 20866.6667 | -11770.3333
240 | 1 | 50 | 208 | 1.5 | 23122 |  |  | 13866.6667 | -9255.3333
240 | 1 | 37.5 | 156 | 1.5 | 17351 |  |  | 10400 | -6951
240 | 1 | 25 | 104 | 1.5 | 11574 |  |  | 6933.3333 | -4640.6667
208 | 3 | 2500 | 6950 | 4 | 154444 |  |  | 173750 | 19306
208 | 3 | 2000 | 5552 | 4 | 123377 |  |  | 138800 | 15423
208 | 3 | 1500 | 4164 | 3.5 | 132190 |  |  | 118971.4286 | -13218.5714
208 | 3 | 1000 | 2776 | 3.5 | 88167 |  |  | 79314.2857 | -8852.7143
208 | 3 | 750 | 2082 | 3.5 | 66095 |  |  | 59485.7143 | -6609.2857
208 | 3 | 500 | 1388 | 1.24 | 124373 |  |  | 111935.4839 | -12437.5161
208 | 3 | 300 | 833 | 1.11 | 83383 |  |  | 75045.045 | -8337.955
208 | 3 | 225 | 625 | 1.12 | 62004 |  |  | 55803.5714 | -6200.4286
208 | 3 | 150 | 416 | 1.07 | 43198 |  |  | 38878.5047 | -4319.4953
208 | 3 | 112.5 | 312 | 1.11 | 31259 |  |  | 28108.1081 | -3150.8919
208 | 3 | 100 | 278 | 1.11 | 27828 |  |  | 25045.045 | -2782.955
208 | 3 | 75 | 208 | 1 | 20821 |  |  | 20800 | -21
208 | 3 | 50 | 139 | 1 | 9652 |  |  | 13900 | 4248
208 | 3 | 25 | 69 | 1 | 4791 |  |  | 6900 | 2109
600V | 3 | 2500 | 2406 | 4 | 66822 |  |  | 60150 | -6672
600V | 3 | 2000 | 1925 | 4 | 53461 |  |  | 48125 | -5336
600V | 3 | 1500 | 1443 | 3.5 | 57261 |  |  | 41228.5714 | -16032.4286
600V | 3 | 1000 | 962 | 3.5 | 38180 |  |  | 27485.7143 | -10694.2857
600V | 3 | 750 | 722 | 3.5 | 28410 |  |  | 20628.5714 | -7781.4286
600V | 3 | 500 | 482 | 1.3 | 51362 |  |  | 37076.9231 | -14285.0769
600V | 3 | 300 | 289 | 1.2 | 33426 |  |  | 24083.3333 | -9342.6667
600V | 3 | 225 | 217 | 1.2 | 25082 |  |  | 18083.3333 | -6998.6667
600V | 3 | 150 | 145 | 1.2 | 16759 |  |  | 12083.3333 | -4675.6667
600V | 3 | 112.5 | 108 | 1 | 15000 |  |  | 10800 | -4200
600V | 3 | 75 | 72.2 | 1 | 15000
FEEDER LOOKUP
AMP | GA | CONDUIT | GROUND
380 | 500 | 3" | 3
335 | 400 | 2-1/2" | 3
310 | 350 | 2-1/2" | 3
285 | 300 | 2-1/2" | 4
255 | 250 | 2-1/2" | 4
230 | 4/0 | 2" | 4
200 | 3/0 | 2" | 6
175 | 2/0 | 2" | 6
150 | 1/0 | 1-1/2" | 6
130 | 1 | 1-1/4" | 6
115 | 2 | 1-1/4" | 6
100 | 3 | 1-1/4" | 8
70 | 4 | 1" | 8
55 | 6 | 3/4" | 8
40 | 8 | 3/4" | 10
30 | 10 | 1/2" | 10
20 | 12 | 1/2" | 12
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
ALUMINUM | FEEDERS |  |  | AMPS TABLE 310.16 60º C 0-100A 75º C 100A+ | 3-PHASE Z(LN)/1000' PER TABLE 9 0.85 PF STEEL C (WORST CASE!) | SERVICE GROUND & SEC OF XFRM TABLE 250.66 PER FEEDER SIZE | EQUIPMENT GROUND TABLE 250.122 PER OCPD | CONDUIT FILL TABLE C.1 5+ WIRES | CONDUIT FILL TABLE C.9 5+ WIRES | CONCATENATE SETS & WIRE SIZE
COPPER | OCPD | SETS | WIRE SIZE | AL | AL | AL | AL | EMT | PVC | Excel stuff |  | AL TABLE= | A81:J114
1 | 6000 | 20 | 500 | 6200 | 0.064 | 250 | 3-400 | 3 | 3.5 | 20500 |  | CU TABLE= | A115:J146
2 | 5000 | 17 | 500 | 5270 | 0.064 | 250 | 3-400 | 3 | 3.5 | 17500
3 | 4000 | 13 | 500 | 4030 | 0.064 | 250 | 2-400 | 3 | 3.5 | 13500 | C4->
4 | 3000 | 10 | 500 | 3100 | 0.064 | 250 | 2-300 | 3 | 3.5 | 10500 | C6->
5 | 2500 | 9 | 500 | 2790 | 0.064 | 250 | 2-300 | 3 | 3.5 | 9500
6 | 2000 | 8 | 350 | 2000 | 0.08 | 250 | 400 | 3 | 3 | 8350 | #N/A
7 | 1600 | 6 | 400 | 1620 | 0.073 | 250 | 350 | 3 | 3.5 | 6400
8 | 1200 | 4 | 500 | 1240 | 0.064 | 250 | 250 | 3 | 3.5 | 4500
9 | 1000 | 4 | 350 | 1000 | 0.08 | 4/0 | 4/0 | 3 | 3 | 4350
10 | 800 | 3 | 400 | 810 | 0.073 | 4/0 | 3/0 | 3 | 3.5 | 3400
11 | 700 | 3 | 350 | 750 | 0.08 | 4/0 | 3/0 | 3 | 3 | 3350
12 | 600 | 2 | 500 | 620 | 0.064 | 4/0 | 2/0 | 3 | 3.5 | 2500
13 | 500 | 2 | 350 | 500 | 0.08 | 3/0 | 1/0 | 3 | 3 | 2350
14 | 450 | 2 | 300 | 460 | 0.088 | 3/0 | 1/0 | 2.5 | 3 | 2300
15 | 400 | 2 | 250 | 410 | 0.1 | 1/0 | 1 | 2.5 | 3 | 2250
16 | 350 | 2 | 4/0 | 360 | 0.11 | 1/0 | 1 | 2.5 | 2.5 | 24/0
17 |  | 1 | 500 | 310 | 0.064 | 1/0 | 1 | 3 | 3.5 | 1500
18 |  | 1 | 400 | 270 | 0.073 | 1/0 | 2 | 3 | 3.5 | 1400
19 |  | 1 | 350 | 250 | 0.08 | 1/0 | 2 | 3 | 3 | 1350
20 |  | 1 | 300 | 230 | 0.088 | 1/0 | 2 | 2.5 | 3 | 1300
21 |  | 1 | 250 | 205 | 0.1 | 2 | 4 | 2.5 | 3 | 1250
22 |  | 1 | 4/0 | 180 | 0.11 | 2 | 4 | 2.5 | 2.5 | 14/0
23 |  | 1 | 3/0 | 155 | 0.14 | 4 | 4 | 2 | 2.5 | 13/0
24 |  | 1 | 2/0 | 135 | 0.16 | 4 | 4 | 2 | 2 | 12/0
25 |  | 1 | 1/0 | 100 | 0.2 | 6 | 6 | 2 | 2 | 11/0
26 |  | 1 | 1 | 85 | 0.25 | 6 | 6 | 1.5 | 2 | 11
27 |  | 1 | 2 | 75 | 0.3 | 6 | 6 | 1.25 | 1.5 | 12
28 |  | 1 | 3 | 65 | 0.37 | 6 | 6 | 1.25 | 1.25 | 13
29 |  | 1 | 4 | 55 | 0.46 | 6 | 8 | 1.25 | 1.25 | 14
30 |  | 1 | 6 | 40 | 0.72 | 6 | 8 | 1 | 1 | 16
31 |  | 1 | 8 | 35 | 1.1 | 6 | 8 | 0.75 | 1 | 18
32 |  | 1 | 10 | 25 | 1.8 | 6 | 8 | 0.75 | 0.75 | 110
33 |  | 1 | 12 | 15 | 2.8 | 6 | 12 | 0.75 | 0.5 | 112
1 | 6000 | 16 | 500 | 6080 | 0.05 | 3/0 | 2-400 | 3 | 3.5 | 16500
2 | 5000 | 14 | 500 | 5320 | 0.05 | 3/0 | 2-350 | 3 | 3.5 | 14500
3 | 4000 | 11 | 500 | 4180 | 0.05 | 3/0 | 500 | 3 | 3.5 | 11500
4 | 3000 | 8 | 500 | 3040 | 0.05 | 3/0 | 400 | 3 | 3.5 | 8500
5 | 2500 | 7 | 500 | 2660 | 0.05 | 3/0 | 350 | 3 | 3.5 | 7500
6 | 2000 | 6 | 400 | 2010 | 0.056 | 3/0 | 250 | 3 | 3.5 | 6400
7 | 1600 | 5 | 400 | 1675 | 0.056 | 3/0 | 4/0 | 3 | 3.5 | 5400
8 | 1200 | 4 | 350 | 1240 | 0.06 | 3/0 | 3/0 | 3 | 3 | 4350
9 | 1000 | 3 | 400 | 1005 | 0.056 | 3/0 | 2/0 | 3 | 3.5 | 3400
10 | 800 | 3 | 300 | 855 | 0.065 | 2/0 | 1/0 | 2.5 | 3 | 3300
11 | 700 | 3 | 250 | 765 | 0.073 | 2/0 | 1/0 | 2.5 | 3 | 3250
12 | 600 | 2 | 350 | 620 | 0.06 | 2/0 | 1 | 3 | 3 | 2350
13 | 500 | 2 | 250 | 510 | 0.073 | 1/0 | 2 | 2.5 | 3 | 2250
14 | 450 | 2 | 4/0 | 460 | 0.08 | 1/0 | 2 | 2.5 | 2.5 | 24/0
15 | 400 | 2 | 3/0 | 400 | 0.094 | 1/0 | 3 | 2 | 2.5 | 23/0
16 |  | 1 | 500 | 380 | 0.05 | 1/0 | 1 | 3 | 3.5 | 1500
17 |  | 1 | 400 | 335 | 0.056 | 1/0 | 1 | 3 | 3.5 | 1400
18 |  | 1 | 350 | 310 | 0.06 | 2 | 1 | 3 | 3 | 1350
19 |  | 1 | 300 | 285 | 0.065 | 2 | 4 | 2.5 | 3 | 1300
20 |  | 1 | 250 | 255 | 0.073 | 2 | 4 | 2.5 | 3 | 1250
21 |  | 1 | 4/0 | 230 | 0.08 | 2 | 4 | 2.5 | 2.5 | 14/0
22 |  | 1 | 3/0 | 200 | 0.094 | 4 | 6 | 2 | 2.5 | 13/0
23 |  | 1 | 2/0 | 175 | 0.11 | 4 | 6 | 2 | 2 | 12/0
24 |  | 1 | 1/0 | 150 | 0.13 | 6 | 6 | 2 | 2 | 11/0
25 |  | 1 | 1 | 130 | 0.16 | 6 | 6 | 1.5 | 2 | 11
26 |  | 1 | 2 | 115 | 0.2 | 8 | 8 | 1.25 | 1.5 | 12
27 |  | 1 | 3 | 100 | 0.24 | 8 | 8 | 1.25 | 1.25 | 13
28 |  | 1 | 4 | 70 | 0.3 | 8 | 8 | 1.25 | 1.25 | 14
29 |  | 1 | 6 | 55 | 0.45 | 8 | 10 | 1 | 1 | 16
30 |  | 1 | 8 | 40 | 0.7 | 8 | 10 | 0.75 | 1 | 18
31 |  | 1 | 10 | 30 | 1.1 | 8 | 10 | 0.75 | 0.75 | 110
32 |  | 1 | 12 | 20 | 1.7 | 8 | 12 | 0.75 | 0.5 | 112
STD OCPD NEC 240.6
6000
5000
4000
3000
2500
2000
1600
1200
1000
800
700
600
500
450
400
350
300
250
225
200
175
150
125
110
100
90
80
70
60
50
45
35
30
25
20
15