## 14K 2021 CANADIAN PROTOTYPE
PLUMBING FIXTURE SCHEDULE
FIXTURE DATA | [10 empty] | FAUCET DATA |  |  |  | PLUMBING FIXTURE SPECIFICATION
MARK | DESCRIPTION | LOCATION | MANUFACTURER | MODEL | CONNECTION | [5 empty] | MODEL | MANUFACTURER | CW | HW
[5 empty] | CW | HW | TRAP | WASTE | VENT | GALLONS
BFP-1 | BACKFLOW PREVENTER | FISH PREP | WILKINS | 34-975XL-S | 3/4" | [9 empty] | 3/4" BACKFLOW WITH Y STRAINER
AG-1 | AIR GAP | FISH PREP | WILKINS | AG4 | [10 empty] | 3/4" AIR GAP
| PRESSURE REDUCING VALVE | FISH PREP | WILKINS | 34-600G | [10 empty] | 3/4" TAPPED AND ASSEMBLED REGULATOR 92-25 A GAUGE LEAD FREE
DBP-1 | DOMESTIC WATER BOOSTER PUMP | RECEIVING | GRUNDFOS | CMBE COMPACT BOOSTER PUMP #CMBE 10-54-I-U-C-E-D-G 1x220-240V 50/60H - 98548118 | 1 1/2" | [9 empty] | BOOSTER PUMP ASSEMBLY PIPING CONNECTIONS TO THE 11/2" DOMESTIC WATER RISER SHALL INCLUDE A 11/2" QUARTER TURN BALL VALVE BY-PASS. THE BOOSTER PUMP ASSEMBLY SHALL OPERATE AT 220-240V/1PH AND SHALL BE FACTORY ASSEMBLED, WIRED AND TESTED PACKAGE PRESSURE BOOSTING SYSTEM. THE BOOSTER SYSTEM SHALL BE A FLAG FRAME MOUNTED PACKAGE CONSISTING OF A 2 HP 1/60/200-240V MOTOR, STAINLESS STEEL EN 1.4301 AISI 304 PUMP HOUSING AND IMPELLER(2) AND PRE-PIPED 0.528 GALLON TANK. THE SYSTEM SHALL BE SHIPPED WITH ALL COMPONENTS, SOME ASSEMBLY MAY BE REQUIRED. FOLLOW THE MANUFACTURER'S INSTALLATION INSTRUCTION FOR PROPER ASSEMBLY, SHELF MOUNTED ON THE WALL AT 4'-0" AFF. THE SYSTEM SHALL BE CSA/ULC LISTED. THE PUMP SHALL BE SIZED FOR 26 GPM WITH A 26 PSI BOOST. ELECTRICAL DESIGN IS BASED ON A SINGLE 240V, 1 PHASE, 2 HP PUMP. COORDINATE WITH THE ELECTRICAL CONTRACTOR IF PUMP HORSEPOWER IS DIFFERENT.
EWC-1 | ELECTRIC WATER COOLER | HALL A | OASIS | PG8ACSLU-U | 1/2" |  | 1 1/4"-1 1/2" | 2" | 1 1/2" | [5 empty] | TWO STATION BI-LEVEL WALL MOUNT WATER COOLER, BARRIER-FREE ACCESS FRONT ONLY EASY TOUCH CONTROL, MOUNT WITH HIGH UNIT ON LEFT
EWC-2 | ELECTRIC WATER COOLER INSTALL KIT | HALL A | HJC | EWC KIT | [10 empty] | STOP, ESCUTCHEON, SS BRAIDED HOSE (LEAD FREE) W/ 1-1/4" CHROME P-TRAP w/CO
EWC-3 | ELECTRIC WATER COOLER CHECK VALVE | HALL A | WATTS | FLF7RU2-2 | [10 empty] | 1/2" FEM IPxUN DUAL CHECK VALVE (LEAD FREE)
ET-1 | EXPANSION TANK | RECEIVING | ZURN | XT-35 | 3/4" | [9 empty] | NON-ASME EXPANSION TANK, 9.0 GAL., INSTALL PER MANUFACTURER'S INSTRUCTIONS, FOR TWO TANK WATER SYSTEM.
FCO-1 | FLOOR CLEANOUT | SEE LOCATIONS ON DRAWINGS | ZURN | ZN1400-4NH-HD
FD-1 | FLOOR DRAIN | RESTROOMS, RECEIVING | ZURN | ZN415 5B-3NP |  |  | 3" | 3" | 1 1/2" | [5 empty] | 3" CAST IRON BODY FLOOR DRAIN W/ 5" DIA. ADJUSTABLE NICKEL BRONZE STRAINER HEAD W/ 1/2" TRAP PRIMER TAP.
FD-2 | FLOOR DRAIN | RECEIVING | ZURN | ZN505-4NH-HP-VP |  |  | 4" | 4" | 2" | [5 empty] | 4" CAST IRON BODY FLOOR DRAIN W/ 12" POLISHED NICKEL BRONZE TOP, HEEL-PROOF GRATE & VANDAL-PROOF SECURED TOP, 1/2" TRAP PRIMER TAP 3"
HB-1 | EXTERIOR HOSE BIB | EXTERIOR OF BUILDING | ZURN | Z1321-XL | 3/4" | [9 empty] | NON-FREEZE CERAMIC CONTROL W/ INTEGRAL VACUUM BREAKER (SEMI RECESSED) FOR MINIMUM 10" WALL THICKNESS.
HT-1 | HAIR INTERCEPTOR | BATHING AREA | J.R. SMITH | 8790 |  |  |  | 4" | [6 empty] | HAIR INTERCEPTOR WITH YOKE TYPE COVER, TO BE INSTALLED IN MINIMUM 12"x16" VAULT WITH NON-SLIP FLOOR FASTENER COVER.
HT-1 | HAIR INTERCEPTOR | BATHING AREA | J.R. SMITH | 8790 |  |  |  | 4" | [6 empty] | HAIR INTERCEPTOR WITH YOKE TYPE COVER, TO BE INSTALLED IN MINIMUM 12"x16" VAULT WITH NON-SLIP FLOOR FASTENER COVER.
L-1 | LAVATORY | WASHROOMS | ZURN | Z5344 |  |  |  | 2" | 1 1/2" | [5 empty] | WHT VC 20x18 3H 4CC , WALL HUNG BARRIER FREE W/ FRONT OVERFLOW
LF-1 | LAVATORY FAUCET | WASHROOMS | ZURN | Z86500-XL | 1/2" | 1/2" | [8 empty] | 4" CC SLOW CLOSING METERING CHROME-PLATED BRASS FAUCET BODY.
|  | WASHROOMS | HJC | LAV KIT (LEAD-FREE) | [10 empty] | STOPS, ESTUCHEONS, SS BRAIDED SUPPLIES (LEAD-FREE), 1 1/4" CHROME P-TRAP w/ CO & 1 1/4" OPEN GRID STRAINER KIT
LDT-1 | ADA TRAP WRAP | WASHROOMS | ZURN | Z8946-1 | [10 empty] | PROTECTIVE COVER
| LAVATORY CARRIER | WASHROOMS | ZURN | Z1321 (EZ-D) | [10 empty] | ZURN Z1231-EZD BACK-TO-BACK LAVATORU CARRIER OR Z1231 SINGLE LAVATORY CARRIER
MPS-1 | MULTI-PURPOSE SINK | HOLDING #1, HOLDING #2, FISH EQUIPMENT | MUSTEE | 15F |  |  | 2" | 2" | 1 1/2" | [5 empty] | SINGLE COMPARTMENT 19 GALLON SINK, ONE-PIECE MOLDED CONSTRUCTION, 34"H x 23"W x 23 1/2"D. ACCOMMODATES DUAL HANDLE FAUCET W/4" CENTER. HEAVY GAUGE STEEL LEGS WITH BUILT-IN LEVELERS. SECURE LEGS TO FLOOR.
MPSF-1 | MULTIPURPOSE SINK FAUCET | HOLDING #1, HOLDING #2, FISH EQUIPMENT | ZURN | Z812M4-XL-SS1B | 1/2' | 1/2" | [8 empty] | 4" CC DECK MOUNT SERVICE SINK FAUCET (LEAD FREE)
MS-1 | MOP SINK | RECEIVING | ZURN | Z1996-24 |  |  |  | 3" | 1 1/2" | [5 empty] | MOLDED HIGH DENSITY COMPOSITE BASIN 24"x24"x10" DEEP, 3" DRAIN. PROVIDE ZURN Z8946-1 PROTECTIVE COVERS, SINGLE LEVER SUPPLY.
|  | RECEIVING | ACORN | TILING FLANGE | [10 empty] | TILING FLANGE FOR 24" MOP BASIN (2ea/BASIN). FLAGES ADDED TO SINK BY CONTRACTOR ON SITE.
MSF-1 | MOP SINK FAUCET | RECEIVING | ZURN | Z843M1-XL | 3/4" | 3/4" | [8 empty] | 8" POLISHED CHROME WALL FAUCET
|  | RECEIVING | ZURN | Z1996-MH | [10 empty] | 24" STAINLESS STEEL MOP HANGER C/W 3 RUBBER TOOL GRIPS FITTING W/ GRID STRAINER
MV-1 | MIXING VALVE | RECEIVING | POWERS | LFMM434-10 | 1 1/2" | 1 1/2" | [8 empty] | LEAD FREE POWERS THERMOSTATIC MIXING VALVE (LEAD-FREE), TOP INLET TOP OUTLET, SET AT 110°F, FOR TWO TANK WATER HEATER SYSTEM.
P-1 | BACKFLOW PREVENTER | RECEIVING | WATTS | LF919-QT | 1 1/2" | [9 empty] | REDUCED PRESSURE BACKLFOR PREVENTER ON MAIN INCOMING 1 1/2" LINE, QUARTER TURN VALVES, BRONZE STRAINER, LEAD-FREE CONSTRUCTION.
|  | RECEIVING | WATTS | LF777SI | [10 empty] | STRAINER
|  | RECEIVING | WATTS | 919AGF | [10 empty] | AIR GAP
|  | RECEIVING | WATTS | 919ELF | [10 empty] | ELBOW
RD-1 | ROOF DRAIN | ROOF | ZURN | Z101 |  |  |  | 8" | [6 empty] | 20" DIA. ROOF DRAIN, DURA-COATED CAST IRON BODY WITH COMBINATION MEMBRANE FLASHING CLAMP/GRAVEL GUARD AND LOW SILHOUETTE CAST IRON DOME. WITH UNDER DECK CLAMP ASSEMBLY, SUMP DRAIN RECEIVER, METAL LOCKING DOME AND ADJUSTABLE EXTENSION SLEEVE
RH-1 | ROOF HYDRANT | ROOF | WOODFORD | RH-MS | 3/4" | [9 empty] | RH-MS 1 FPT ROOF HYDRANT MNT SYS F/Non-Freeze Area
|  |  | WOODFORD | SRH | 3/4" | [9 empty] | SRH SAN MODEL ROOF HYDRANT
RP-1 | RECIRCULATING PUMP | RECEIVING | BELL & GOSSETT | NBF-22U |  | 3/4" | [8 empty] | BRONZE BODY LUBRICATED CIRCULATORPUMP (90 WATTS), 115V, 1∅, 3000 RPM 2GPM @ 12 F.O.W. C/W 113201LF UNION SET
|  | RECEIVING | BELL & GOSSETT | 113201LF | [10 empty] | 3/4" 1/2 UNION SET LEAD-FREE
RPA-1 | RECIRCULATING PUMP AQUASTAT | RECEIVING | BELL & GOSSETT | 113224 AQS-3/4 |  | 3/4" | [8 empty] | 3/4" AQUASTAT
S-1 | SINK | ADOPTIONS, ASSOCIATE RESOURCES | COMPONENT HARDWARE | CH1011FM |  |  | 1 1/2" | 2" | 1 1/2" | [5 empty] | 20 GAUGE S.S. SINK, 19.5"x19"x5.5", 3 HOLE PUNCHING.
SF-1 | SINK FAUCET | ADOPTIONS, ASSOCIATE RESOURCES | ZURN | Z831C4-XL-2F | 1/2" | 1/2" | [8 empty] | 8" CC GOOSENECK DECK FAUCET W/ 4" BLADE HANDLES POLISHED CHROME (LEAD FREE)
|  | ADOPTIONS, ASSOCIATE RESOURCES | HJC | SS LAV KIT | [10 empty] | STOPS, ESTUCHEONS, SS BRAIDED SUPPLIES (LEAD-FREE), 1 1/2" CHROME P-TRAP w/ CO KIT & ML102EZ NON-ADA LAV GUARD
|  | ADOPTIONS, ASSOCIATE RESOURCES | MAINLINE | MLB120AF | [10 empty] | 3/8" x 1/2" x 20" BRAIDED SUPPLY
|  | ADOPTIONS, ASSOCIATE RESOURCES | COMPONENT HARDWARE | FP1 | [10 empty] | SS SINK STRAINER E38-410541-CAN x/ 1 1/2" TAIL PIECE
|  | ADOPTIONS, ASSOCIATE RESOURCES | ZURN | Z8946-1 | [10 empty] | PROTECTIVE COVER
SST-1 | WALL FAUCET | BATHING AREA | ZURN | Z843 L-1 90 YJ | 3/4" | 3/4" | [8 empty] | POLISHED CHROME 8" WASH DOWN FAUCET C/W VACUUM BREAKER SPOUT, INTEGRAL HOSE THREADED SPOUT, VANDAL RESISTANT COLOUR CODED LEVER HANDLES. REFER TO DETAIL ON DRAWING P2.0.
|  | BATHING AREA | ZURN | 700XL 3/4" | [10 empty] | 3/4" DUAL CHECK VALVE ON BOTH HOT & COLD WATER LINES
|  | BATHING AREA | ZURN | LF009-QT-FS | [10 empty] | 1/2" REDUCED PRESSURE ZONE ASSEMBLY MOUNTED DIRECTLY BELOW AND TIGHT TO BOTTOM OF FAUCETS AS REQUIRED BY LOCAL PLUMBING INSPECTOR.
TD-1 | TRENCH DRAIN | BATHING/DRYING AREA | ZURN | Z886 HPP-GL-(2) E1-U4-JC/DB |  |  | 4" | 4" | 2" | [5 empty] | 7 LINEAR FEET EACH. 6" WIDE PRE-SLOPED TRENCH DRAIN, W/ INTEGRAL TOP FRAME, INTERLOCKING ENDS & RADIUSED BOTTOM, PM886HPP HEEL-PROOF POLYETHYLENE GRATE, U4 BOTTOM OUTLET (1 PER TD) AND END CAP (2 PER TD), ZURN P6-DB BOTTOM DOME STRAINER, PPP PTRAP PRIMER ADAPTPR PPPA-4P500 4"x1/2"
TD-2 | TRENCH DRAIN | FISH EQUIPMENT | ZURN | Z886 (2)E1 U3 SPECIAL |  |  | 3" | 3" | 2" | [5 empty] | FOOT TRENCH (1 SECTION 8606N) 10" WITH REBAR CLIPS @ CENTER WITHOUT GRATE. 6"x10"x8"DEEP. GRATE TO BE FLUSHED WITH FINISHED FLOOR, NO-LIP.
TG-1 | THERMOMETER | RECEIVING | MILJOCO | B259951-2W | [10 empty] | 2.5" DIA. THERMOMETER 30 DEGREES-250 DEGREES.
TP-1 | TRAP PRIMER | SEE LOCATIONS ON DRAWINGS | PRECISION PLUMBING PRODUCTS (PPP) | P1-500 WITH TAPPED P-TRAP ADAPTER | 1/2" | [9 empty] | TRAP PRIMER VALVE WITH INTEGRAL BACKFLOW PREVENTER & VACUUM BREAKER PORT PROVIDE DISTRIBUTION UNIT AS REQUIRED. ROUTE 1/2" PEX POLYETHYLENE TUBING DOWN IN WALL AND BELOW SLAB TO P-TRAP, SEE DETAIL ON P2.0, INCLUDE TAPPED P-TRAP ADAPTER. PLUG UNUSED DISTRIBUTION PORTS.
TPD-1 | TRAP PRIMER DISTRIBUTION | SEE LOCATIONS ON DRAWINGS | PPP | DU-U | [10 empty] | DISTRIBUTION UNIT
U-1 | URINAL | MENS RESTROOM | ZURN | Z5755-U | 3/4" |  |  | 2" | 2" | [5 empty] | WHITE VITREOUS CHINE, TOP SPUD VC URINAL, .125 GPF
UF-1 | URINAL FLUSH VALVE | MENS RESTROOM | ZURN | Z6003WS1YB | [10 empty] | URINAL FLUSH VALVE
WB-1 | ICE BOX MAKER OUTLET BOX | ASSOCIATE RESOURCES | SIOUX CHIEF | 696-1010MF | 1/2" | [9 empty] | 1/2 INSWT/SWT ABS ON BOX TOILET DISHWASHER OUTLET BOX WITH MINI RESTER AND LED FREE FRAME.
WBC-1 | ICE BOX MAKER OUTLET BOX CHECK VALVE | ASSOCIATE RESOURCES | WATTS | LF7RU2-2 | [10 empty] | 1/2" DUAL CHECK VALVE ON SUPPLY LINE (LEAD-FREE)
WC-1 | WATER CLOSET | WASHROOMS | AMERICAN STANDARD | CADET 3483.001.020 | 1/2" |  | 3" | 2" | [6 empty] | FLOOR MOUNTED VITREOUS CHINA LOW CONSUMPTION 1.1 GPF PRESSURE ASSIST, SIPHON JET FLUSH ACTION, RIGHT HEIGHT ELONGATED WATER CLOSET, 12" ROUGH-IN
|  | WASHROOMS | AMERICAN STANDARD | 4142.601.020 | [10 empty] | 1.1 GPF LEFT-HAND TRIP LEVER - TAN w/ VANDAL-PROOF LOCKING LID
|  | WASHROOMS | AMERICAN STANDARD | 4142.901.020 | [10 empty] | 1.1 GPF RIGHT-HAND TRIP LEVER - TAN w/ VANDAL-PROOF LOCKING LID
|  | WASHROOMS | CENTOCO | 820STS | [10 empty] | HEAVY-DUTY WHITE ELONGATED OPEN-FRONT w/COVER PLASTIC TOILET SEAT
|  | WASHROOMS | JONES | CLOSET PAK | [10 empty] | WAX RING w/ HORN, CLOSET BOLT SET
WH-1 | WATER HEATER | RECEIVING | RHEEM | EG50C-12, 600V/3/12KW | 1 1/2" |  |  |  |  | 50 |  |  |  |  | WATER HEATER(S) SHALL BE MODEL EG50C-12-G, MANUFACTURED BY RHEEM-RUUD, HAVING ELECTRICAL INPUT OF 575V/3∅/12 KW AND A RECOVERY RATE OF 50 GPH @28°C TEMPERATURE RISE. WATER HEATER(S) SHALL HAVE A STORAGE CAPACITY OF 50 GALLONS. WATER HEATER(S) SHALL HAVE THE CSA SEAL OF CERTIFICATION AND BE FACTORY EQUIPPED WITH AN CSA/ASME RATED TEMPERATURE AND PRESSURE RELIEF. TANK(S) SHALL HAVE A DOUBLE COATING OF HIGH TEMPERATURE PORCELAIN ENAMEL AND FURNISHED WITH MAGNESIUM ANODE RODS RIGIDLY SUPPORTED. WATER HEATER(S) SHALL MEET OR EXCEED THE STANDBY LOSS REQUIREMENTS OF ASHRAE. TANK(S) SHALL HAVE A WORKING PRESSURE OF 150 PSI, AND SHALL BE COMPLETELY ASSEMBLED. WATER HEATER(S) SHALL BE EQUIPPED WITH STAINLESS STEEL SCREW-IN TYPE ELEMENTS. TANK SHALL BE INSULATED WITH THICK POLYURETHANE FOAM INSULATION. WATER HEATER(S) SHALL BE CONSTRUCTED WITH A SYSTEM SENTINEL ELEMENT DIAGNOSTIC PANEL UTILIZING LIGHT EMITTING DIODES. EACH LED WILL CORRESPOND TO THE NUMBER AND LOCATION OF THE HEATING ELEMENTS AND MONITOR THEIR ON-OFF FUNCTION. WATER HEATER(S) SHALL BE PROVIDED WITH MAGNETIC CONTACTORS, 240V CONTROL CIRCUIT TRANSFORMER AND IMMERSION THERMOSTAT(S) WITH MANUAL RESET HIGH LIMIT CONTROL. 11/2" INLET AND OUTLET WATER CONNECTIONS FOR 50 THROUGH 120 GALLON MODELS SHALL BE PROVIDED. WATER HEATER(S) SHALL BE COVERED BY A THREE YEAR LIMITED WARRANTY AGAINST TANK LEAKS.
WHV-1 | WATER HEATER VACUUM RELIEF | RECEIVING | WATTS | LFN36-M1 | [10 empty] | LEAD FREE VACUUM RELIEF VALVE
WH-2 | WATER HEATER | RECEIVING | RHEEM | EG50C-12, 600V/3/12KW | 1 1/2" |  |  |  |  | 50 |  |  |  |  | WATER HEATER(S) SHALL BE MODEL EG50C-12-G, MANUFACTURED BY RHEEM-RUUD, HAVING ELECTRICAL INPUT OF 575V/3∅/12 KW AND A RECOVERY RATE OF 50 GPH @28°C TEMPERATURE RISE. WATER HEATER(S) SHALL HAVE A STORAGE CAPACITY OF 50 GALLONS. WATER HEATER(S) SHALL HAVE THE CSA SEAL OF CERTIFICATION AND BE FACTORY EQUIPPED WITH AN CSA/ASME RATED TEMPERATURE AND PRESSURE RELIEF. TANK(S) SHALL HAVE A DOUBLE COATING OF HIGH TEMPERATURE PORCELAIN ENAMEL AND FURNISHED WITH MAGNESIUM ANODE RODS RIGIDLY SUPPORTED. WATER HEATER(S) SHALL MEET OR EXCEED THE STANDBY LOSS REQUIREMENTS OF ASHRAE. TANK(S) SHALL HAVE A WORKING PRESSURE OF 150 PSI, AND SHALL BE COMPLETELY ASSEMBLED. WATER HEATER(S) SHALL BE EQUIPPED WITH STAINLESS STEEL SCREW-IN TYPE ELEMENTS. TANK SHALL BE INSULATED WITH THICK POLYURETHANE FOAM INSULATION. WATER HEATER(S) SHALL BE CONSTRUCTED WITH A SYSTEM SENTINEL ELEMENT DIAGNOSTIC PANEL UTILIZING LIGHT EMITTING DIODES. EACH LED WILL CORRESPOND TO THE NUMBER AND LOCATION OF THE HEATING ELEMENTS AND MONITOR THEIR ON-OFF FUNCTION. WATER HEATER(S) SHALL BE PROVIDED WITH MAGNETIC CONTACTORS, 240V CONTROL CIRCUIT TRANSFORMER AND IMMERSION THERMOSTAT(S) WITH MANUAL RESET HIGH LIMIT CONTROL. 11/2" INLET AND OUTLET WATER CONNECTIONS FOR 50 THROUGH 120 GALLON MODELS SHALL BE PROVIDED. WATER HEATER(S) SHALL BE COVERED BY A THREE YEAR LIMITED WARRANTY AGAINST TANK LEAKS.
WHV-2 | WATER HEATER VACUUM RELIEF | RECEIVING | WATTS | LFN36-M1 | [10 empty] | LEAD FREE VACUUM RELIEF VALVE
PETSHOTEL PLUMBING FIXTURE SCHEDULE
FIXTURE DATA | [10 empty] | FAUCET DATA |  |  |  | PLUMBING FIXTURE SPECIFICATION
MARK | DESCRIPTION | LOCATION | MANUFACTURER | MODEL | CONNECTION | [5 empty] | MODEL | MANUFACTURER | CW | HW
[5 empty] | CW | HW | TRAP | WASTE | VENT | GALLONS
DS-1 | UNDER COUNTER SANITIZER | PREP | LAMBER-EURODIB | EURODIB F99EKDPS |  | 3/4" |  | 1 1/4" | [6 empty] | EURODIB, UNDER COUNTER SANITIZER, STAINLESS STEEL CONSTRUCTION, WITH BOOSTER, RINSE, DRAIN & SOAP PUMPS. PROVIDE WATER HAMMER ARRESTOR. PROVIDE SANITIZER LISTED AIR GAP FITTING.
ET-1 | EXPANSION TANK | PREP | ZURN | XT-35 | 3/4" | [9 empty] | PROVIDE ONE ZURN MODEL XT-35, 9.0 GAL. EXPANSION TANK, INSTALL PER MANUFACTURER'S INSTRUCTIONS, FOR TWO TANK WATER SYSTEM.
FD-1 | FLOOR DRAIN | PREP, CRATE CLEANING, CRATE STORAGE | ZURN | ZN415B-5B-3NH-P |  |  | 3" | 3" | 1 1/2" | [5 empty] | CAST IRON BODY W/ 5"ø ADJ. NICKEL BRONZE STRAINER HEAD. PROVIDE 1/2" TRAP PRIMER & DEEP SEAL TRAP.
FD-3 | CLAW PROOF FLOOR DRAIN | HOTEL SUITES, PREP, ATRIUM, PLAY ROOMS, TRAINING | ZURN | ZN415B-124-4NH-P |  |  | 4" | 4" | 2" | [5 empty] | CAST IRON BODY WITH 4" NO-HUB BOTTOM OUTLET, COMBINATION INVERTIBLE MEMBRANE CLAMP AND ADJUSTABLE COLLAR WITH SEEPAGE SLOTS, TYPE B POLISHED NICKEL BRONZE LIGHT DUTY STRAINER WITH CLAW PROOF MESH AND 1/2" PRIMER CONNECTION WITH DEEP SEAL P-TRAP.
GD-1 | GARBAGE DISPOSAL | PREP | BADGER 5 InSinkErator | 79008A-ISE | [10 empty] | 1/2 HP HEAVY DUTY DISPOSER W/ CORD, GALVANIZED STEEL CONSTRUCTION, WALL SWITCH OPERATION 120V SINGLE PHASE, INSTALL AT (KS-1) SINK IN PREP
HB-2 | HOSE BIB FOR ECOLAB | PREP | ZURN | Z1341XL-P12-PC |  | 3/4" | [8 empty] | POLISHED CHROME PLATED CAST BRASS BEDPAN WASHER WITH A QUARTER TURN CERAMIC DISC CARTRIDGE AND 21/2" VACUUM BREAKER SPOUT WITH AN INTEGRAL 3/4" HOSE THREADED OUTLET
KS-1 | KITCHEN SINK | PREP | ELKAY | DLR372210 |  |  | 2" | 2" | 2" | [5 empty] | S.S. 10" DEEP DOUBLE BOWL SINK, WITH WINGTIP HANDLES FOR 1.5 GPM FAUCET.
KSF-1 | KITCHEN SINK FAUCET | PREP | ZURN | Z812U4-XL | 1/2" | 1/2" | [8 empty] | FAUCET W/ 4" WRIST BLADE HANDLE
MV-1 | MIXING VALVE | PREP | POWERS | LFMM432-1 | 1 1/2" | 1 1/2" | [8 empty] | PROVIDE ONE POWERS HYDROGUARD MIXING VALVE, TOP INLET TOP OUTLET, SET AT 110°F, FOR TWO TANK WATER HEATER SYSTEM.
RP-1 | RECIRCULATING PUMP | PREP | BELL & GOSSETT | NBF-22U |  | 3/4" | [8 empty] | BRONZE BODY LUBRICATED CIRCULATOR 90 WATTS, 115V, 1∅, 3000 RPM 2GPM @ 12 F.O.W. WITH B&G AQUASTAT MODEL AQS-3/4
SST-1 | WALL FAUCET | CRATE CLEANING | ZURN | Z843L1-90-YJ | 3/4" | 3/4" | [8 empty] | POLISHED CHROME 8" WASH DOWN FAUCET C/W VACUUM BREAKER SPOUT, INTEGRAL HOSE THREADED SPOUT, VANDAL RESISTANT COLOUR CODED LEVER HANDLES. PROVIDE ZURN WILKINS MODEL 700XL 3/4" DUAL CHECK VALVE ON BOTH HOT & COLD WATER LINES. PROVIDE WATTS SERIES LF009QT (1/2") REDUCED PRESSURE ZONE ASSEMBLY MOUNTED DIRECTLY BELOW AND TIGHT TO BOTTOM OF FAUCETS AS REQUIRED BY LOCAL PLUMBING INSPECTOR. REFER TO DETAIL ON DRAWING P2.0.
TP-1 | TRAP PRIMER | SEE LOCATIONS ON DRAWINGS | PPP | P1-500 WITH TAPPED P-TRAP ADAPTER | 1/2" | [9 empty] | TRAP PRIMER VALVE WITH INTEGRAL BACKFLOW PREVENTER & VACUUM BREAKER PORT PROVIDE DISTRIBUTION UNIT AS REQUIRED. ROUTE 1/2" PEX POLYETHYLENE TUBING DOWN IN WALL AND BELOW SLAB TO P-TRAP, SEE DETAIL ON P2.0, INCLUDE TAPPED P-TRAP ADAPTER. PLUG UNUSED DISTRIBUTION PORTS.
WB-2 | WASHING MACHINE OUTLET BOX | PREP | OATEY | 38934 | 3/4" | [9 empty] | (2) 1/4" BALL VALVES *TOP MOUNTED), SWEAT CONNECTION WITH VACUUM BREAKERS, PLASTIC BOX, REFER TO SHEET P2.0 FOR DRAIN PUNCH-OUT INFORMATION
WF-1 | WATER FILTER | PREP | ENVIRONMENTAL WATER SYSTEMS | SS-2.5 | 1/2" | [9 empty] | WATER FILTER 2.5 GPM MAX FLOW RATE, MAX PRESSURE 125 PSIG, UNIT SIZE 4"x16", UP TO 10,000 GALLON CAPACITY, STEEL BRACKET. GC TO PROVIDE 6 REPLACEMENT FILTERS, MODEL F.SET.SS-2.56, PROVIDE LAMINATED INSTRUCTIONS. REFER TO 16/P2.0.
|  | PREP | ENVIRONMENTAL WATER SYSTEMS | F. SET.SS-2.56 | [10 empty] | FILTER REPLACEMENT (6 PER SYSTEM)
WC-2 | WATER CLOSET | PREP | CAROMA | CARAVELLE SYDNEY SMART II 305 | 1/2" |  |  | 3" | 2" | [5 empty] | FLOOR MOUNTED VITREOUS CHINA 1.28/0.8 GPM WATER SAVING DUAL FLUSH HIGH EFFICIENCY TOILET (HET), TWO PIECE ULTRA LOW FLUSH (ULF), W/ VANDAL RESISTANT KIT #413276, PROVIDED CAROMA OPEN FACE SEAT.
WH-3 | ELECTRIC WATER HEATER | PREP | RHEEM | EG50C-12-G | 1 1/2" | [9 empty] | WATER HEATER(S) SHALL BE MODEL EG50C-12-G, MANUFACTURED BY RHEEM-RUUD, HAVING ELECTRICAL INPUT OF