## Project Info
Project | Petsmart
Store # | 3306
Location | Oshawa Windfields
Address | 2605 Simcoe Street North, Oshawa, ON, L1H 7K4
Planned Lease Area | 11231
Similar store ???
U/S of Roof Deck | 19'-4"
U/s of Joists | 17'-8"
U/s of beams | 17'-1"
U/S Reinf. Structure | 16'-1"

## Ventilation Calculations
VENTILATION AIR CALCULATIONS
SPACE | AREA (SQ.FT.) | OCCUPANT LOAD (PERSONS) | OCCUPANCY CLASSIFICATION | REQUIRED VENTILATION AIR (PER PERSON) | REQUIRED VENTILATION AIR (PER SQ.FT.) | TOTAL VENTIALTION AIR REQUIRED (CFM) | REQUIRED EXHAUST AIR (PER PERSON) | MINIMUM REQUIRED EXHAUST AIR (PER SQ.FT.) | MINIMUM EXHAUST AIR REQUIRED (CFM) | TOTAL EXHAUST AIR PROVIDED (CFM) | TOTAL SUPPLY AIR PROVIDED (CFM) | TOTAL VENTILATION AIR PROVIDED (CFM) | SYSTEM(S) PROVIDING OUTDOOR AIR (UNIT MARK) |  | Supply Air | O/A Air | %
Adoptions | 130 | 2 | Specialty Shops (Pet Shops - Animal Areas) | 7.5 | 0.18 | 38.4 | N/A | 1.5 | 195 | 200 | 150 | 46.5 | RTU-5 AND EF-3 | RTU-1 | 2400 | 600 | 0.25
Adoptions Meet & Greet | 78 | 1 | Specialty Shops (Pet Shops - Animal Areas) | 7.5 | 0.18 | 21.54 | N/A | 1.5 | 117 | 200 | 150 | 29.5 | RTU-5 AND EF-3
Associate Resources | 265 | 5.352 | Office Buildings -Breakrooms | 5 | 0.12 | 58.5601 | N/A | 0.25 | 66.25 | 150 | 600 | 89 | RTU-5 AND EF-3
Bathing | 117 | 2.363 | Animal Facilities -Animal Preparation Rooms | 10 | 0.18 | 44.6897 | N/A | 1.5 | 175.5 | 500 | 375 | 58.2432 | RTU-3 AND EF-2 | RTU-2 | 1600 | 368 | 0.23 | 1600
Computer/Copy | 118 | 1 | Office Buildings -Breakrooms | 5 | 0.12 | 19.16 | N/A | 0.25 | 29.5 | 350 | 200 | 30 | RTU-1 AND EF-1
Drying | 389 | 10 | Animal Facilities -Animal Preparation Rooms | 10 | 0.18 | 170.02 | N/A | 1.5 | 583.5 | 1125 | 1125 | 189.7297 | RTU-3 AND EF-2 | RTU-3 | 1850 | 460 | 0.24865 | 1850
Fish Equipment / Prep | 372 | 10 | Retail -Pet Shops (Animal Areas) | 7.5 | 0.18 | 141.96 | N/A | 0.9 | 334.8 | 600 | 1250 | 205.5 | RTU-5 AND EF-3 | RTU-4 | 3000 | 750 | 0.25
Hall 'A' | 98 | N/A | Public Spaces (Corridors) | N/A | N/A | 0 | N/A | N/A | 0 | 0 | 150 | 40 | RTU-3
Holding #1 | 90 | 1.8177 | Animal Facilities -Small Animal Cage Rm (Ventilated) | 10 | 0.18 | 34.3767 | N/A | 1.5 | 135 | 150 | 125 | 41.25 | RTU-5 AND EF-3 | RTU-5 | 2400 | 600 | 0.25
Holding #2 | 92 | 1.8581 | Animal Facilities -Small Animal Cage Rm (Ventilated) | 10 | 0.18 | 35.1406 | N/A | 1.5 | 138 | 150 | 125 | 42.25 | RTU-5 AND EF-3 | RTU-6 | 3000 | 750 | 0.25
BOPIS Closet | 83 | 1.6763 | Office Buildings -Office Space | 5 | 0.06 | 13.3615 | N/A | N/A | 0 | 0 | 300 | 30 | RTU-1 | RTU-7 | 3000 | 750 | 0.25
Universal Washroom | 102 | 2.06 | Toilets -Public | N/A | N/A | 0 | N/A | 50 (Exh.)* | 50 | 150 | 100 | 20 | RTU-3 AND EF-4 | RTU-8 | 2000 | 460 | 0.23
Manager / Vault | 113 | 2.2822 | Office Buildings -Office Space | 5 | 0.06 | 18.1909 | N/A | N/A | 0 | 0 | 200 | 29 | RTU-1
P.O.S | 200 | 5.0218 | Retail -Sales | 7.5 | 0.12 | 61.6634 | N/A | N/A | 0 | 0 | 500 | 68 | RTU-4 |  | 19250 | 4738
Receiving | 1384 | 4.5921 | Miscellaneous -Warehouse | 10 | 0.06 | 128.9606 | N/A | N/A | 0 | 50 | 2000 | 190 | RTU-8
Sales Area Front | 3118 | 78.2896 | Retail -Sales | 7.5 | 0.12 | 961.3321 | N/A | N/A | 0 | 0 | 3300 | 1235 | RTU-4 AND RTU-1
Sales Area Rear | 5675 | 142.4931 | Retail -Sales | 7.5 | 0.12 | 1749.6984 | N/A | N/A | 0 | 0 | 6000 | 2013 | RTU-6 AND RTU-7
Salon | 392 | 7.917 | Retail -Pet Shops (Animal Areas) | 7.5 | 0.18 | 129.9371 | N/A | 0.9 | 352.8 | 200 | 1300 | 150 | RTU-2
Salon Check-in | 289 | 5.8367 | Retail -Sales | 7.5 | 0.12 | 78.4555 | N/A | N/A | 0 | 0 | 300 | 108 | RTU-2
Vestibule | 176 | 3.5545 | Retail -Sales | 7.5 | 0.12 | 47.7791 | N/A | N/A | 0 | 0 | 900 | 103 | RTU-1
Unisex Washroom | 94 | 1.8985 | Toilets -Public | N/A | N/A | 0 | N/A | 50 (Exh.)* | 50 | 150 | 100 | 20 | RTU-3 AND EF-4
TOTALS | 13375 |  |  |  |  | 3753.2256 |  |  | 2227.35 | 3975 | 19250 | 4737.973
* = Required Minimum Exhaust air is 50 CFM per code. 100 CFM Exhaust Air is Provided.
** = 100% Exhaust with RTU
NOTE: CALCULATIONS OF THE REQUIRED EXHAUST AND VENITLATION AIR IS BASED ON THE LATEST EDITION OF ASHRAE 62.1